## Data Entry Form
Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Typing KB | Typing KB/Look Up | Typing KB | Typing KB | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB | Typing KB | Typing KB | Typing KB | Drop Down | Typing KB | Typing KB | Drop Down | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB | Drop Down | Typing KB | Drop Down | Drop Down | Typing KB | Drop Down | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB
Location | Station ID | Station Name | Town | Street | Cross Street | Feature Mark Number | Feature Length (feet) | From Circuit | To Circuit | From Series | To Series | Feature | Feature Type | Comments | Job Number/Work Order/Purchase Order # | Feature Install Date | Feature Construction Type | Outside Diameter | OD Record Identifier 1 | OD Record Identifier 2 | Wall Thickness | WT Record Identifier 1 | WT Record Identifier 2 | Seam Type | Seam Weld Record Identifier 1 | Seam Weld Record Identifier 2 | Grade | Grade Record Identifier 1 | Grade Record Identifier 2 | Specification | Rating Class | Rating Class Record Identifier 1 | Rating Class Record Identifier 2 | OD 2 | WT 2 | Material Type | Coating Type | Coating Description | Manufacturer | MFR Model Number | Class Exceptions | Current Class Location | Established Operating Pressure | Pressure Test Record Identifier
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 1 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original Construction | 24 | 1 | 2 | 0.375 | 2 | None | ERW | 2 | None | X42 | 2 | None | API 5L | None | None | None | None | None | Steel | Fusion Bond Epoxy | None | Stupp | Unknown | None | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 2 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original Construction | 24 | 1 | 2 | 0.375 | 2 | None | ERW | 2 | None | X42 | 2 | None | API 5L | None | None | None | None | None | Steel | Fusion Bond Epoxy | None | Stupp | Unknown | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 3 | 50 | 1 | 1 | 1000 | 1000 | Valve | Ball |  |  | 2001-02-12 | Original Construction | 24 | 1 | 2 | None | None | None | None | None | None | None | None | None | ANSI | ANSI 300 | 3 | None | None | None | None | None | None | None | None | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 4 | 50 | 1 | 1 | 2000 | 2000 | Flange | Weld Neck | Raised Face |  | 2001-02-12 | Original Construction | 24 | 1 | 2 | None | None | None | None | None | None | None | None | None | ANSI | ANSI 300 | 3 | None | None | None | None | None | None | None | None | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 5 | 50 | 1 | 1 | 3000 | 3000 | Elbow | Socket Weld | 1D, 1.5D, 3D radius elbow |  | 2001-02-12 | Original Construction | 24 | 1 | 2 | None | None | None | None | None | None | None | None | None | None | 3000 LB | 3 | None | None | None | None | None | None | None | None | Fabrication | Class 3 | 150 | 4

## Build-QC Display
Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Typing KB | Typing KB/Look Up | Typing KB | Typing KB | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB |  |  | Look Up | Typing KB | Typing KB | Typing KB |  |  | Look Up | Drop Down | Typing KB | Typing KB |  |  | Look Up | Drop Down | Typing KB | Typing KB |  |  | Look Up | Drop Down | Drop Down | Typing KB | Typing KB |  |  | Look Up | Drop Down | Typing KB | Drop Down | Drop Down | Typing KB | Drop Down | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB
Location (PipelineSystemItem/PipeSystemID) | Station ID (PipelineItem) | Station Name (StationName) | Town (Town) | Street (Street) | Cross Street (CrossStreet) | Feature Mark Number | Feature Length (feet) | From Circuit | To Circuit | From Series | To Series | Feature | Feature Type | Comments | Job Number/Work Order/Purchase Order # | Feature Install Date | Feature Construction Type | Outside Diameter | OD Record Identifier 1 | OD Record Identifier 2 | OD Record Identifier 1 Doc Type (DocumentTypeItem) | OD Record Identifier 2 Doc Type (DocumentTypeITem) | OD Matrix Check | Wall Thickness | WT Record Identifier 1 | WT Record Identifier 2 | WT Record Identifier 1 Doc Type (DocumentTypeItem) | WT Record Identifier 2 Doc Type (DocumentTypeItem) | WT Matrix Check | Seam Type | Seam Weld Record Identifier 1 | Seam Weld Record Identifier 2 | Seam Weld Record Identifier 1 Doc Type (DocumentTypeItem) | Seam Weld Record Identifier 2 Doc Type (DocumentTypeItem) | Seam Matrix Check | Grade | Grade Record Identifier 1 | Grade Record Identifier 2 | Grade Record Identifier 1 Doc Type (DocumentTypeItem) | Grade Record Identifier 2 Doc Type (DocumentTypeItem) | Grade Matrix Check | Specification | Rating Class | Rating Class Record Identifier 1 | Rating Class Record Identifier 2 | Rating Class Record Identifier 1 Doc Type (DocumentTypeItem) | Rating Class Record Identifier 2 Doc Type | Rating Class Matrix Check (DocumentTypeItem) | OD 2 | WT 2 | Material Type | Coating Type | Coating Description | Manufacturer | MFR Model Number | Class Exceptions | Current Class Location | Established Operating Pressure | Pressure Test Record Identifier
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 1 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original | 24 | 1 | 2 |  |  |  | 0.375 | 2 | None |  |  |  | ERW | 2 | None |  |  |  | X42 | 2 | None |  |  |  | API 5L | None | None | None |  |  |  | None | None | Steel | Fusion Bond Epoxy | None | Stupp | Unknown | None | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 2 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original | 24 | 1 | 2 |  |  |  | 0.375 | 2 | None |  |  |  | ERW | 2 | None |  |  |  | X42 | 2 | None |  |  |  | API 5L | None | None | None |  |  |  | None | None | Steel | Fusion Bond Epoxy | None | Stupp | Unknown | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 3 | 50 | 1 | 1 | 1000 | 1000 | Valve | Ball |  |  | 2001-02-12 | Original | 24 | 1 | 2 |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | ANSI | ANSI 300 | 3 | None |  |  |  | None | None | None | None | None | None | None | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 4 | 50 | 1 | 1 | 2000 | 2000 | Flange | Weld Neck | Raised Face |  | 2001-02-12 | Original | 24 | 1 | 2 |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | ANSI | ANSI 300 | 3 | None |  |  |  | None | None | None | None | None | None | None | In Station | Class 3 | 150 | 4
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 5 | 50 | 1 | 1 | 3000 | 3000 | Elbow | Socket Weld | 1D, 1.5D, 3D radius elbow |  | 2001-02-12 | Original | 24 | 1 | 2 |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | None | None | None |  |  |  | None | 3000 LB | 3 | None |  |  |  | None | None | None | None | None | None | None | Fabrication | Class 3 | 150 | 4
NL-44

## Sheet1
<th>ANSI Rating</th>
<th>Class Exceptions</th>
<th>Coating Desc.</th>
<th>Coating Type</th>
<th>Construction Type</th>
<th>Cross Street</th>
<th>Current Class Location</th>
<th>Delete</th>
<th>Estab. Op. Pressure</th>
<th>Feature Install Date</th>
<th>Feature Mark Number</th>
<th>Feature Number</th>
<th>Feature Type</th>
<th>Feature</th>
<th>From Circuit</th>
<th>From Series</th>
<th>Grade RecID 1 DocType</th>
<th>Grade RecID 1</th>
<th>Grade RecID 2 DocType</th>
<th>Grade RecID 2</th>
<th>Grade</th>
<th>Job Number / Work Order / Purchase Order #</th>
<th>Length (feet)</th>
<th>Location</th>
<th>Manufacturer</th>
<th>Material Type</th>
<th>MFR Model Number</th>
<th>Notes / Comments</th>
<th>O.D. 1 (inch)</th>
<th>OD 2 (inch)</th>
<th>OD RecID 1 DocType</th>
<th>OD RecID 1</th>
<th>OD RecID 2 DocType</th>
<th>OD RecID 2</th>
<th>PT Documnet</th>
<th>Rating RecID 1 DocType</th>
<th>Rating RecID 1</th>
<th>Rating RecID 2 DocType</th>
<th>Rating RecID 2</th>
<th>Seam RecID 1 DocType</th>
<th>Seam RecID 1</th>
<th>Seam RecID 2 DocType</th>
<th>Seam RecID 2</th>
<th>Seam Weld Type</th>
<th>Specifiction</th>
<th>Station ID</th>
<th>Station Name</th>
<th>Street</th>
<th>To Circuit</th>
<th>To Series</th>
<th>Town</th>
<th>W.T. 1 (inch)</th>
<th>WT 2 (inch)</th>
<th>WT RecID 1 DocType</th>
<th>WT RecID 1</th>
<th>WT RecID 2 DocType</th>
<th>WT RecID 2</th>
<th>Actions</th>

## Sheet2
1 | ILI | NL-44 | N/A | Hicksville | Charlotte Ave. | John St. | 11 | 12 | 1 | 1 | 1000 | 2000 | Pipe | Casing | Unknown |  | Unknown | 6.625 | 003884E4.pdf | 003820C3.pdf | 003884E4.pdf | 003884E4.pdf | Butt Weld or Continuous Weld | 003884E4.pdf | 003820CA.pdf | WPL6 | 003884E3.pdf | 003884E3.pdf | API 5LS | ANSI 400 | 003820CA.pdf | 003820CA.pdf | 0.405 | Concrete | Bare | Unknown | ArkLa | 2 | Delete
Edit
Insert
2 | ILI | NL-44 | N/A | Hicksville | Charlotte Ave. | John St. |  | 60 | 1 | 1 | 2000 | 3000 | Field Bend | Bending Machine | 123 | 1999-01-01 | Original Construction | 1.05 | 003820C3.pdf | 003884E3.pdf | 003884E3.pdf | 003843F3.pdf | Butt Weld or Continuous Weld | 003843FC.pdf | 003820CA.pdf | WPL9 | 00384415.pdf | 00384415.pdf | ASTM A234 | ASA 900 | 00384415.pdf | 003843F3.pdf | 4.5 | PVC | Extruded Polyethylene | Unknown | All American | 2 | Delete

## MAOP Report
Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Station Information, manual entry 1 time in SQL or Front End Loading | Typing KB | Typing KB/Look Up | Typing KB | Typing KB | Typing KB | Typing KB | Drop Down | Drop Down | Typing KB |  | Typing KB | Drop Down | Drop Down | Typing KB | Typing KB | Look Up | Typing KB | Typing KB | Typing KB | Look Up | Drop Down | Typing KB | Typing KB | Look Up | Drop Down | Typing KB | Typing KB | Look Up | Drop Down | Drop Down | Typing KB | Typing KB | Look Up | Drop Down | Typing KB | Drop Down | Drop Down | Typing KB | Drop Down | Typing KB | Drop Down | Drop Down | Look Up | Look Up | Look Up | Typing KB | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up | Look Up
Location | Station ID | Station Name | Town | Street | Cross Street | Feature Mark Number | Feature Length (feet) | From Circuit | To Circuit | From Series | To Series | Feature | Feature Type | Comments | Job Number/Work Order/Purchase Order # | Feature Install Date | Feature Construction Type | Outside Diameter | OD Record Identifier 1 | OD Record Identifier 2 | OD Matrix Check | Wall Thickness | WT Record Identifier 1 | WT Record Identifier 2 | WT Matrix Check | Seam Type | Seam Weld Record Identifier 1 | Seam Weld Record Identifier 2 | Seam Matrix Check | Grade | Grade Record Identifier 1 | Grade Record Identifier 2 | Grade Matrix Check | Specification | Rating Class | Rating Class Record Identifier 1 | Rating Class Record Identifier 2 | Rating Class Matrix Check | OD 2 | WT 2 | Material Type | Coating Type | Coating Description | Manufacturer | MFR Model Number | Class Exceptions | Current Class Location | SMYS [S] | Design Factor [F] | Joint Factor [E] | Established Operating Pressure | Governing MAOP | DP TVC | HT TVC | DP and HT TVC | DP of Pipe 192.619 (a)(1) | Test Pressure 192.619 (a)(2) | PT Min Test Pressure | PT Test Medium | PT Date | PT Duration (Hours) | Instrument/Dead Weight Elevation | Min Elevation | Max Elevation | PT Hydrotest Name and Location | Pressure Recording Charts | Test Instrument Calibration | Operator Name | PT Person Responsible | PT Test Company Name | PT Document
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 1 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original | 24 |  |  |  | 0.375 |  |  |  | ERW |  |  |  | X42 |  |  |  | API 5L | None |  |  |  | None | None | Steel | Fusion Bond Epoxy | None | Stupp | None | None | Class 3 | 42000 | 0.5 | 1 | 150 | 656 | No | Yes | No | 656.25 | 763.33 | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 2 | 50 | 1 | 1 | 1000 | 1000 | Pipe | No Casing |  |  | 2001-02-12 | Original | 24 |  |  |  | 0.375 |  |  |  | ERW |  |  |  | X42 |  |  |  | API 5L | None |  |  |  | None | None | Steel | Fusion Bond Epoxy | None | Stupp | None | In Station | Class 3 | 42000 | 0.5 | 1 | 150 | 656 | No | Yes | No | 656.25 | 763.33 | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 3 | 50 | 1 | 1 | 1000 | 1000 | Valve | Ball |  |  | 2001-02-12 | Original | 24 |  |  |  | None |  |  |  | None |  |  |  | None |  |  |  | ANSI | ANSI 300 |  |  |  | None | None | None | None | None | None | None | In Station | Class 3 | None | None | None | 150 | 740 | No | Yes | No | 740 | 763.33 | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 4 | 50 | 1 | 1 | 2000 | 2000 | Flange | Weld Neck | Raised Face |  | 2001-02-12 | Original | 24 |  |  |  | None |  |  |  | None |  |  |  | None |  |  |  | ANSI | ANSI 300 |  |  |  | None | None | None | None | None | None | None | In Station | Class 3 | None | None | None | 150 | N/A | No | No | No | None | N/A | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf
UPNY | 824-116 | Pottery Rd | Warners | 6548 Pottery Rd Off PL36 | N/A | 5 | 50 | 1 | 1 | 3000 | 3000 | Elbow | Socket Weld | 1D, 1.5D, 3D radius elbow |  | 2001-02-12 | Original | 24 |  |  |  | None |  |  |  | None |  |  |  | None |  |  |  | None | 3000 LB |  |  |  | None | None | None | None | None | None | None | Fabrication | Class 3 | None | None | None | 150 | N/A | No | No | No | None | N/A | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf
unknown from here ->
n/a from here <-

## Material Records
MATERIAL RECORDS INFORMATION
RECORDS IDENTIFIER | DOC TYPE | FILE NAME | DRAWING NUMBER | REVISION NUMBER | PAGE NUMBER
1 | As-Built Drawings | 246S03.pdf
2 | (Pipe) Mill Test Report | 3-27-01 MTRs for 24in x .375 wall pipe.PDF
3 | As-Built Drawings | B2-A32-38246.pdf
4 | Stand Alone Record_Quality Record

## Pressure Test Records
[7 empty] | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data | Rec ID call this data
Records Identifier | Feature Mark Number | Feature Length (feet) | From Circuit | To Circuit | From Series | To Series | PT Min Test Pressure | PT Test Medium | PT Date | PT Duration (Hours) | Instrument/Dead Weight Elevation | Min Elevation | Max Elevation | PT Hydrotest Name and Location | Pressure Recording Charts | Test Instrument Calibration | Operator Name | PT Person Responsible | PT Test Company Name | PT Document
4 | [6 empty] | 1145 | Water | 2001-08-24 | 24 | 0 | 0 | 0 | Anhydrous HCL System-Oyster Creek | Yes | Yes | None | Buck Epley | PipeLogic Services, LLC | DPL246 HT-01-137 circuit OC to Plt B.pdf

## Issues-Errors
Feature Number | Description of Issue: Builder | Description of Issue: QC | Description of Issue: Engineer

## Records Matrix - NatGrid
Note: The record matrix only applies to pipe and non-rated fittings. Rated Fittings (flange, valve…) is considered TVC as long as there's at least 1 record of any doc type.
| Outside Diameter |  | Stand Alone - Quality Record | Before Construction (BC) | [8 empty] | After Construction (AC)
|  |  |  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
| Before Contstruction | Pipe Specification | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Bill of Materials | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Purchase Order | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Pressure Test Plan | [12 empty] | x | x | x | x | x | x | x | x | x
Weld Procedures
|  | Material Transfer/Delivery Tags/Packing List | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
Design/Contract Specifications
Job Estimate Face Sheet
|  | Invoices | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
| After Construction | (MTR) Mill Test Report | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x | x
Material Inspection Report
|  | Pressure Test Report |  | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x | x | x | x | x | x
|  | As-Built Redlines |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
|  | As-Built Survey Notes | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
|  | As-Built Drawings | x | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
|  | Completion Report |  | x | x | x | x |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x
|  | Pipeline Inspection Report | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x |  | x | x | x
|  | Pipeline Replacement Report | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x | x
|  | ILI Report | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x |  | x
|  | NDE Reports (X-Ray/UT) | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x | x
|  | Weld Map/Detail | [10 empty] | x
ASME History of Line Pipe (North America)
Pipe Manufacturer
|  | Pipe Manufactured year | remove
| Specified Minimum Yield Strength (GRADE) |  | Stand Alone - Quality Record | Before Construction (BC) | [8 empty] | After Construction (AC)
|  |  |  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
| Before Contstruction | Pipe Specification | [10 empty] | x |  | x | x | x | x | x |  | x
|  | Bill of Materials | [10 empty] | x |  | x | x | x | x | x |  | x
|  | Purchase Order | [10 empty] | x |  | x | x | x | x | x |  | x
|  | Pressure Test Plan | [13 empty] | x | x | x | x |  | x
Weld Procedures
|  | Material Transfer/Delivery Tags/Packing List | [10 empty] | x |  | x | x | x | x | x |  | x
Design/Contract Specifications
Job Estimate Face Sheet
|  | Invoices | [10 empty] | x |  | x | x | x | x | x | x | x
| After Construction | (MTR) Mill Test Report | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  |  | x |  |  | x
Material Inspection Report
|  | Pressure Test Report |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x
|  | As-Built Redlines |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x
|  | As-Built Survey Notes | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x
|  | As-Built Drawings |  | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x
|  | Completion Report |  | x | x | x | x |  | x |  |  | x |  |  |  | x | x | x |  |  | x
|  | Pipeline Inspection Report | [9 empty] | x |  |  |  | x | x | x
|  | Pipeline Replacement Report | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x
ILI Report
NDE Reports (X-Ray/UT)
|  | Weld Map/Detail | [10 empty] | x
ASME History of Line Pipe (North America)
Pipe Manufacturer
|  | Pipe Manufactured year | remove
| Wall Thickness |  | Stand Alone - Quality Record | Before Construction (BC) | [8 empty] | After Construction (AC)
|  |  |  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
| Before Contstruction | Pipe Specification | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Bill of Materials | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Purchase Order | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | Pressure Test Plan | [13 empty] | x | x | x | x | x | x
Weld Procedures
|  | Material Transfer/Delivery Tags/Packing List | [10 empty] | x |  | x | x | x | x | x |  | x | x | x
Design/Contract Specifications
Job Estimate Face Sheet
|  | Invoices | [10 empty] | x |  | x | x | x | x | x | x | x | x | x
| After Construction | (MTR) Mill Test Report | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x | x | x | x | x | x | x
Material Inspection Report
|  | Pressure Test Report |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x | x | x
|  | As-Built Redlines |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
|  | As-Built Survey Notes | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
|  | As-Built Drawings |  | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
|  | Completion Report |  | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x |  | x | x | x | x
|  | Pipeline Inspection Report |  | x | x | x | x |  |  |  |  | x | x |  |  | x | x | x | x |  | x | x
|  | Pipeline Replacement Report | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x
|  | ILI Report |  | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x | x | x
|  | NDE Reports (X-Ray/UT) |  | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x
|  | Weld Map/Detail | [10 empty] | x
ASME History of Line Pipe (North America)
Pipe Manufacturer
|  | Pipe Manufactured year | remove
| Seam Weld Type |  | Stand Alone - Quality Record | Before Construction (BC) | [8 empty] | After Construction (AC)
|  |  |  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
| Before Contstruction | Pipe Specification | [10 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | Bill of Materials | [10 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | Purchase Order | [10 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | Pressure Test Plan | [10 empty] | x |  |  | x | x | x | x |  | x
Weld Procedures
|  | Material Transfer/Delivery Tags/Packing List | [22 empty] | x
Design/Contract Specifications
Job Estimate Face Sheet
|  | Invoices | [10 empty] | x |  |  | x | x | x | x | [5 empty] | x
| After Construction | (MTR) Mill Test Report | x | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  | x | x
Material Inspection Report
|  | Pressure Test Report | [13 empty] | x | x | x |  |  | x
|  | As-Built Redlines |  | x | x | x | x |  |  |  |  | x | x |  | x |  | x |  | x |  | x |  |  |  | x
|  | As-Built Survey Notes | x | x | x | x | x |  |  |  |  | x | x |  | x | x |  |  | x |  | x |  |  |  | x
|  | As-Built Drawings |  | x | x | x | x |  |  |  |  | x | x |  | x |  |  |  | x |  | x |  |  |  | x
|  | Completion Report |  | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  |  | x
Pipeline Inspection Report
|  | Pipeline Replacement Report | x | x | x | x | x | [5 empty] | x |  | x | x | x | x | x | [5 empty] | x
ILI Report
NDE Reports (X-Ray/UT)
|  | Weld Map/Detail | [10 empty] | x
1 |  | ASME History of Line Pipe (North America) |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x | x |  | x |  |  |  |  | x | x
|  | Pipe Manufacturer | [22 empty] | x
|  | Pipe Manufactured year | remove | [21 empty] | x
| Rating Class |  | Stand Alone - Quality Record | Before Construction (BC) | [8 empty] | After Construction (AC)
|  |  |  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report |  | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
| Before Contstruction | Pipe Specification | x
|  | Bill of Materials | x
|  | Purchase Order | x
|  | Pressure Test Plan | x
|  | Weld Procedures | x
|  | Material Transfer/Delivery Tags/Packing List | x
|  | Design/Contract Specifications | x
|  | Job Estimate Face Sheet | x
|  | Invoices | x
| After Construction | (MTR) Mill Test Report | x
|  | Material Inspection Report | x
|  | Pressure Test Report | x
|  | As-Built Redlines | x
|  | As-Built Survey Notes | x
|  | As-Built Drawings | x
|  | Completion Report | x
|  | Pipeline Inspection Report | x
|  | Pipeline Replacement Report | x
|  | ILI Report | x
|  | NDE Reports (X-Ray/UT) | x
|  | Weld Map/Detail | x
|  | ASME History of Line Pipe (North America) | x
|  | Pipe Manufacturer | x
|  | Pipe Manufactured year | remove

## Records Matrix - NatGrid SQL
|  | Code | Record Matrix | Blank | Stand Alone - Quality Record | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags/Packing List | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (MTR) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer
|  | 1001 | Blank
|  | 1001 | Stand Alone - Quality Record | [11 empty] | x |  |  |  | x | x |  | x | x | x | x
|  | 1001 | Pipe Specification | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
Outside Diameter | 1001 | 1001 | Bill of Materials | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
Wall Thickness | 1002 | 1001 | Purchase Order | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
Grade | 1003 | 1001 | Pressure Test Plan | [13 empty] | x | x | x | x | x | x | x | x | x
Seam Weld | 1004 | 1001 | Weld Procedures
Rating Class | 1005 | 1001 | Material Transfer/Delivery Tags/Packing List | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1001 | Design/Contract Specifications
|  | 1001 | Job Estimate Face Sheet
|  | 1001 | Invoices | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1001 | (MTR) Mill Test Report |  | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x | x
|  | 1001 | Material Inspection Report
|  | 1001 | Pressure Test Report |  |  | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x | x | x | x | x | x
|  | 1001 | As-Built Redlines |  |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
|  | 1001 | As-Built Survey Notes |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
|  | 1001 | As-Built Drawings |  | x | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
|  | 1001 | Completion Report |  |  | x | x | x | x |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x
|  | 1001 | Pipeline Inspection Report |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x |  | x | x | x
|  | 1001 | Pipeline Replacement Report |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x | x
|  | 1001 | ILI Report |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x |  | x
|  | 1001 | NDE Reports (X-Ray/UT) |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x | x
|  | 1001 | Weld Map/Detail | [11 empty] | x
|  | 1001 | ASME History of Line Pipe (North America)
|  | 1001 | Pipe Manufacturer
|  | 1002 | Blank
|  | 1002 | Stand Alone - Quality Record | [11 empty] | x |  |  |  | x |  |  |  | x
|  | 1002 | Pipe Specification | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1002 | Bill of Materials | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1002 | Purchase Order | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1002 | Pressure Test Plan | [14 empty] | x | x | x | x | x | x
|  | 1002 | Weld Procedures
|  | 1002 | Material Transfer/Delivery Tags/Packing List | [11 empty] | x |  | x | x | x | x | x |  | x | x | x
|  | 1002 | Design/Contract Specifications
|  | 1002 | Job Estimate Face Sheet
|  | 1002 | Invoices | [11 empty] | x |  | x | x | x | x | x | x | x | x | x
|  | 1002 | (MTR) Mill Test Report |  | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x | x | x | x | x | x | x
|  | 1002 | Material Inspection Report
|  | 1002 | Pressure Test Report |  |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x | x | x
|  | 1002 | As-Built Redlines |  |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
|  | 1002 | As-Built Survey Notes |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
|  | 1002 | As-Built Drawings |  |  | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
|  | 1002 | Completion Report |  |  | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x |  | x | x | x | x
|  | 1002 | Pipeline Inspection Report |  |  | x | x | x | x |  |  |  |  | x | x |  |  | x | x | x | x |  | x | x
|  | 1002 | Pipeline Replacement Report |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x
|  | 1002 | ILI Report |  |  | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x | x | x
|  | 1002 | NDE Reports (X-Ray/UT) |  |  | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x
|  | 1002 | Weld Map/Detail | [11 empty] | x
|  | 1002 | ASME History of Line Pipe (North America)
|  | 1002 | Pipe Manufacturer
|  | 1003 | Blank
|  | 1003 | Stand Alone - Quality Record | [11 empty] | x |  |  |  | x |  |  |  | x
|  | 1003 | Pipe Specification | [11 empty] | x |  | x | x | x | x | x |  | x
|  | 1003 | Bill of Materials | [11 empty] | x |  | x | x | x | x | x |  | x
|  | 1003 | Purchase Order | [11 empty] | x |  | x | x | x | x | x |  | x
|  | 1003 | Pressure Test Plan | [14 empty] | x | x | x | x |  | x
|  | 1003 | Weld Procedures
|  | 1003 | Material Transfer/Delivery Tags/Packing List | [11 empty] | x |  | x | x | x | x | x |  | x
|  | 1003 | Design/Contract Specifications
|  | 1003 | Job Estimate Face Sheet
|  | 1003 | Invoices | [11 empty] | x |  | x | x | x | x | x | x | x
|  | 1003 | (MTR) Mill Test Report |  | x | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  |  | x |  |  | x
|  | 1003 | Material Inspection Report
|  | 1003 | Pressure Test Report |  |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x
|  | 1003 | As-Built Redlines |  |  | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x
|  | 1003 | As-Built Survey Notes |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x
|  | 1003 | As-Built Drawings |  |  | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x
|  | 1003 | Completion Report |  |  | x | x | x | x |  | x |  |  | x |  |  |  | x | x | x |  |  | x
|  | 1003 | Pipeline Inspection Report | [10 empty] | x |  |  |  | x | x | x
|  | 1003 | Pipeline Replacement Report |  | x | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x
|  | 1003 | ILI Report
|  | 1003 | NDE Reports (X-Ray/UT)
|  | 1003 | Weld Map/Detail | [11 empty] | x
|  | 1003 | ASME History of Line Pipe (North America)
|  | 1003 | Pipe Manufacturer
|  | 1004 | Blank
|  | 1004 | Stand Alone - Quality Record | [11 empty] | x |  |  |  | x |  |  |  | x
|  | 1004 | Pipe Specification | [11 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | 1004 | Bill of Materials | [11 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | 1004 | Purchase Order | [11 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
|  | 1004 | Pressure Test Plan | [11 empty] | x |  |  | x | x | x | x |  | x
|  | 1004 | Weld Procedures
|  | 1004 | Material Transfer/Delivery Tags/Packing List | [23 empty] | x
|  | 1004 | Design/Contract Specifications
|  | 1004 | Job Estimate Face Sheet
|  | 1004 | Invoices | [11 empty] | x |  |  | x | x | x | x | [5 empty] | x
|  | 1004 | (MTR) Mill Test Report |  | x | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  | x | x
|  | 1004 | Material Inspection Report
|  | 1004 | Pressure Test Report | [14 empty] | x | x | x |  |  | x
|  | 1004 | As-Built Redlines |  |  | x | x | x | x |  |  |  |  | x | x |  | x |  | x |  | x |  | x |  |  |  | x
|  | 1004 | As-Built Survey Notes |  | x | x | x | x | x |  |  |  |  | x | x |  | x | x |  |  | x |  | x |  |  |  | x
|  | 1004 | As-Built Drawings |  |  | x | x | x | x |  |  |  |  | x | x |  | x |  |  |  | x |  | x |  |  |  | x
|  | 1004 | Completion Report |  |  | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  |  | x
|  | 1004 | Pipeline Inspection Report
|  | 1004 | Pipeline Replacement Report |  | x | x | x | x | x | [5 empty] | x |  | x | x | x | x | x | [5 empty] | x
|  | 1004 | ILI Report
|  | 1004 | NDE Reports (X-Ray/UT)
|  | 1004 | Weld Map/Detail | [11 empty] | x
|  | 1004 | ASME History of Line Pipe (North America) |  |  | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x | x |  | x |  |  |  |  | x
|  | 1004 | Pipe Manufacturer | [23 empty] | x
|  | 1005 | Blank |  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Stand Alone - Quality Record |  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Pipe Specification | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Bill of Materials | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Purchase Order | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Pressure Test Plan | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Weld Procedures | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Material Transfer/Delivery Tags/Packing List | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Design/Contract Specifications | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Job Estimate Face Sheet | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Invoices | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | (MTR) Mill Test Report | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Material Inspection Report | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x
|  | 1005 | Pressure Test Report | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x | x
|  | 1005 | As-Built Redlines | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x | x
|  | 1005 | As-Built Survey Notes | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x | x
|  | 1005 | As-Built Drawings | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x | x
|  | 1005 | Completion Report | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x | x
|  | 1005 | Pipeline Inspection Report | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x | x
|  | 1005 | Pipeline Replacement Report | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x | x
|  | 1005 | ILI Report | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x | x
|  | 1005 | NDE Reports (X-Ray/UT) | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  | x
|  | 1005 | Weld Map/Detail | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
|  | 1005 | ASME History of Line Pipe (North America)
|  | 1005 | Pipe Manufacturer
Note: In addition to the above record pairs, all features applicable to Rating Class Matrix Check [Rated Fittings (flange, valve…)] are considered TVC as long as there's at least 1 record of any doc type.

## LookUp Tables
Feature
Pipe
Branch Connect
Cap
Compressor
Coupling
Cross
Drip
Dust Receiver
Elbow
Field Bend
Flange
Heater
Joint
Manifold
Meter
MFG Bend
Nipple
PCF
Reducer
Regulator
Relief Valve
Saddle
Scrubber
Separator
Sleeve
Strainer
Swage
Tap
Tee
Union
Valve
Other
Feature Type
| Pipe | Branch Connect | Cap | Compressor | Coupling | Cross | Drip | Dust Receiver | Elbow | Field Bend | Flange | Heater | Joint | Manifold | Meter | MFG Bend | Nipple | PCF | Reducer | Regulator | Relief Valve | Saddle | Scrubber | Separator | Sleeve | Strainer | Swage | Tap | Tee | Union | Valve
| Casing | Elbolet | Closure | Other | Other | Other | Other | Other | Bell Bell Chill Ring | Bell Bell Chill Ring | Blind | Gas | Insulating | Forged | Diaphragm | Bell Bell Chill Ring | Other | Bottom Tap | Conc.-Std | Axial Flow | Ball Valve | Other | Gas | Other | Aqua Wrap | Other | Other | Blow-off | Butt Weld | Other | Ball
| No Casing | Nipolet | Pipe | Unknown | Unknown | Unknown | Unknown | Unknown | Forged | Bending Machine | Insulating | Other | Other | Other | Insertion Probe | Butt Weld | Unknown | Line Stopper | Conc.-Ven | Fisher | Block | Unknown | Other | Unknown | Clockspring | Unknown | Unknown | Connection | Cross | Unknown | Block
|  | Sockolet | Weather Cap | [5 empty] | Miter | Int Mandrel-Bending Machine | Lap Joint | Unknown | Unknown | Unknown | Insertion Turbine | Forged |  | Mueller | ECC-Std | Boot Type | Blowdown Valve |  | Unknown |  | Dresser Style 220 |  |  | Connection Curb Valve Tee w/nut | Reducing Tee |  | Butterfly
|  | Thredolet | Weld Cap | [5 empty] | Reducing | Miter | Reducing |  |  |  | Micrometer | Miter |  | Other | ECC-Ven | Diaphragm | Butterfly Valve |  |  |  | Full Sole |  |  | Connection Pin off-Valve Tee | Reducing Y |  | Check
|  | Weldolet | Other | [5 empty] | Rolled Plate | Wrinkle | Slip On |  |  |  | Orifice | Reducing |  | Side Tap | Internal Only | Fire Fuse - Slam Shut | Check Valve |  |  |  | Half Sleeve |  |  | Connection Service Tee | Reinforced Tee |  | Control Ball
|  | Other | Unknown | [5 empty] | Socket Weld | Other | Socket Weld |  |  |  | OrificeSkidMntGasWell | Rolled Plate |  | Stopple | Other | Flex Flow | Control Valve |  |  |  | Half Sole |  |  | Drip-External | Socket Weld |  | Curb Valve Tee w/ nut-Mueller
|  | Unknown | [6 empty] | Wrinkle | Unknown | Threaded |  |  |  | Rotary | Socket Weld |  | TDW | Unknown | HPR Set | Flex Flow Valve |  |  |  | Patch |  |  | Drip-Internal | Straight Tee |  | Gate
[9 empty] | Other |  | Weld Neck |  |  |  | Sonic | Threaded |  | Top Tap |  | Mooney | Gate Valve |  |  |  | PLIDCO - repair clamp |  |  | Insertion Probe | Straight Y |  | Globe
[9 empty] | Unknown |  | Other |  |  |  | Turbine | Wrinkle |  | Other |  | Slam shut | Regulator Valve |  |  |  | Repair |  |  | Save-a-valve | Threaded |  | Plug
[11 empty] | Unknown |  |  |  | Other | Other |  | Unknown |  | Spring | Spring Type |  |  |  | Split Sleeve |  |  | Take-off | Other |  | Service Tee
[15 empty] | Unknown | Unknown |  |  |  | Other | Other |  |  |  | Type A |  |  | Take-off Curb Valve Tee w/ nut | Unknown |  | Other
[20 empty] | Unknown | Unknown |  |  |  | Type B |  |  | Take-off Pin off-Valve Tee |  |  | Unknown
[25 empty] | Other |  |  | Take-off Service Tee
[25 empty] | Unknown |  |  | Thermowell
Other
Unknown
Class Exceptions
None
Fabrication
In Station
Feature Construction Type
Original Construction
Replacement
Unknown
Nominal | OD 1
0.125 | 0.405
0.25 | 0.54
0.375 | 0.675
0.5 | 0.84
0.75 | 1.05
1 | 1.315
1.25 | 1.66
1.5 | 1.9
2 | 2.375
2.5 | 2.875
3 | 3.5
3.5 | 4
4 | 4.5
5 | 5.563
6 | 6.625
8 | 8.625
10 | 10.75
12 | 12.75
14 | 14
16 | 16
18 | 18
20 | 20
22 | 22
24 | 24
26 | 26
28 | 28
30 | 30
32 | 32
34 | 34
36 | 36
42 | 42
Unknown
| Seam Type | E
| Butt Weld or Continuous Weld | 0.6
| Double Submerged Arc Weld | 1
| Electric Flash Weld | 1
| Electric Fusion Weld | 1
| Electric Weld | 1
| ERW | 1
| Seamless | 1
| Seamless (Fitting) | 1
| Spiral Weld | 1
| Submerged Arc Weld | 1
| Unknown > 4 inch | 0.8
| Unknown 4 inch or less | 0.6
| EFW/Seamless | 1
| ERW/Seamless | 1
N/A
Grade
| A25 | 25000
| Grade 1 | 30000
| Grade 3 | 35000
| Grade 6 | 35000
| Grade A | 30000
| Grade B | 35000
| Grade C | 40000
| WPB | 35000
| WPC | 40000
| WPL6 | 35000
| WPL9 | 46000
| X42 | 42000
| X46 | 46000
| X48 | 48000
| X52 | 52000
| X60 | 60000
| X65 | 65000
| X70 | 70000
| Y-42 | 42000
| Y-46 | 46000
| Y-48 | 48000
| Y-52 | 52000
| Y-60 | 60000
| Y-65 | 65000
| Y-70 | 70000
| N/A | 24000
| Unknown | 24000
Specification
ANSI
API 5L
API 5LS
API 5LX
API 6D
ASME
ASTM A105
ASTM A106
ASTM A130
ASTM A234
ASTM A333
ASTM A350
ASTM A381
ASTM A420
ASTM A53/A53M
ASTM A671
ASTM A672
ASTM A691
ASTM D2513-99
ASTM D2517
MSS SP65
MSS SP75
Other
Unknown
Rating Class
| ANSI 150 | 285
| ANSI 300 | 740
| ANSI 400 | 985
| ANSI 600 | 1480
| ANSI 900 | 2220
| ANSI 1500 | 3705
| ANSI 2500 | 6170
| ASA 150 | 275
| ASA 300 | 720
| ASA 400 | 960
| ASA 600 | 1440
| ASA 900 | 2160
| ASA 1500 | 3600
| ASA 2500 | 6000
| WOG 50 | 50
| WOG 100 | 100
| WOG 150 | 150
| WOG 175 | 175
| WOG 200 | 200
| WOG 500 | 500
| WOG 600 | 600
| WOG 720 | 720
| WOG 800 | 800
| WOG 960 | 960
| WOG 1000 | 1000
| WOG 1440 | 1440
| WOG 1500 | 1500
| WOG 2160 | 2160
| WOG 2200 | 2200
| WOG 3000 | 3000
| Class 2000 | 2000
| Class 3000 | 3000
| Class 6000 | 6000
| Class 9000 | 9000
| 50 LB | 50
| 100 LB | 100
| 150 LB | 150
| 200 LB | 200
| 500 LB | 500
| 600 LB | 600
| 720 LB | 720
| 800 LB | 800
| 960 LB | 960
| 1000 LB | 1000
| 1440 LB | 1440
| 1500 LB | 1500
| 2000 LB | 2000
| 2160 LB | 2160
| 2200 LB | 2200
| 3000 LB | 3000
| 6000 LB | 6000
| 9000 LB | 9000
N/A
Unknown
Current Class Location
Class 1
Class 2
Class 3
Class 4
Unknown
HCA
HCA
Non-HCA
Unknown
Document Type
Pipe Specification
Bill of Materials
Purchase Order
Pressure Test Plan
Weld Procedures
Material Transfer/Delivery Tags/Packing List
Design/Contract Specifications
Job Estimate Face Sheet
Invoices
(MTR) Mill Test Report
Material Inspection Report
Pressure Test Report
As-Built Redlines
As-Built Survey Notes
As-Built Drawings
Completion Report
Pipeline Inspection Report
Pipeline Replacement Report
ILI Report
NDE Reports (X-Ray/UT)
Weld Map/Detail
ASME History of Line Pipe (North America)
Pipe Manufacturer
Stand Alone - Quality Record
Other
Coating Type
Asphalt
Asphalt Enamel
Asphalt With Concrete
Bare
BBE
Coal Tar
Coal Tar Enamel
Coal Tar Epoxy
Coal Tar With Concrete
Concrete Coating
Devgrip
Enamel
Epoxy
Extruded Polyethylene
Extruded Polyethylene With Concrete
FBE Abrasion Coating
Fusion Bond Epoxy
Fusion Bond Epoxy ARO With Concrete
Fusion Bond Epoxy With ARO
Fusion Bond Epoxy With Concrete
HAA
Liquid Epoxy
Mastic
Mastic With Concrete
Mobilox
Multi-Component Liquid (e.g. liquid epoxies and/or liquid urethanes)
Paint
PC
PLC
Powercrete
Powercrete J
Protal
SOMA
Tape
Tape With Concrete
Two-Layer Polyethylene
Wax
Wax Tape
XTRUPL
Unknown
Material Type
Steel
Concrete
Copper
Ductile Iron
Fiber Optic
Galvanized
HDPE
Plastic
PVC
Ribbed Polyethylene
Cast Iron
Unknown
Manufacturer
Aerotec
Alberta Phoenix
Algoma
AMERICAN
American Cast Iron Pipe Company
AO Smith
Apollo
ARMCO STEEL
BALON
Benteler
Berg
BERGROHR
Bethlehem Steel
BRITISH STEEL
C.S.I. TUBULAR
Callier Steel Pipe
CAMERON
CAMPIPE
Camrose
Canadian Phoenix or Phoenix
Canadoil Forge
Canadol pipe manufacturer
Cantek
Canterra Energy
Capital Pipe & Steel Products of Canada
CMC STEEL
Comco Distributors
CONFAB
Consolidated Western Steel Corporation
Corus Pipe
CRISPIN
DALLAS
Dalmine
DANIEL
DRESSER
DURABOND STEEL PIPE
Edgen Pipe
EDWARD
ESTEL
Europipe
Evraz Inc
FISHER
FLOWSERVE
Foothills Pipe Lines
FRANCO
FRANCOPB
G.T.S. FRANCE
GENEVA STEEL
GILMORE STEEL
Hoesch
Indutech
International Port. Pipe Mill
INTERPROVENCIAL STEEL & PIPE CORP. LTD
INVASION
Ipsco
Italsider
ITT Grunnell
JFE
JONES & LAUGHLIN
KAISER
Kawasaki Japan
KIKK Kikutani
L.B. FOSTER
LABARGE
Ladish
LING TIMKO VOUGHT
LONE STAR
MANNESMANN (GERMANY)
MARUBENI ITOCHU TUBULARS CANADA LTD.
MAVERICK TUBE CORPORATION
MCEVOY
MITSUBISHI-KAWASAKI
Mooney
MUELLER
Napa
Napco
Naptech
NATIONAL PIPE & TUBE
National Tube
NEWPORT STEEL
NEXTEEL
NIKOH TUBE
Nippon Steel Japan
NKK Corporation Japan
Nordstrom
NORTH STAR STEEL
Northwestern Utilities
Oregon Steel Mills Inc.
PACIFIC PIPE CO
Paige Hersy
PARAGONPIPE
PBV
PIONEER STEEL
Prudential
Quebec Natural Gas
Ram Steel
Republic Steel
ROCKWELL
Sandvik
Shaw
Siderca
South Durham
SOUTHWESTERN PIPE OF COLORADO
Stelco
Stupp
Sumitomo Japan
TAD Metals Italy
Tamsa (Mexico)
TAYLOR FORGE PIPE WORKS
TDW
Tenaris
TERNIUM
Tex Tube
Thomas Pipe
Triton
TUBACERO, S.A. (MEXICO)
Tube Spiral
TUBULAR STEEL
U & M STAR
Union Pipe (Sumitomo Medal IND.)
United States Steel
V & M Star
VALLOUREC
VICTAULIC
VINSONSUPPLY
WALWORTH
Welland Tube
Welspun
Westlund Industrial
WHEATELY
WKM
YALE
Youngstown Tube
Unknown
PT Test Medium
Water
Nitrogen
Natural Gas
Other
Unknown
Pressure Recording Charts
Yes
No
Test Instrument Calibration
Yes
No

## PFL Template Updates
| Variable | Old Value | New Value | Remove | Resolved Date
2018-10-04 | Record Matrix | (pipe) Mill Test Report | (MTR) Mill Test Report
2018-10-04 | Record Matrix | Material Transfer/Delivery Tags | Material Transfer/Delivery Tags/Packing List
2018-10-04 | Record Matrix |  | Stand Alone Record_Quality Record
2018-10-04 | MFR | NORDSTORM | Nordstrom |  | 2018-10-26
2018-10-04 | MFR |  | Apollo |  | 2018-10-26
2018-10-04 | Specification |  | ASTM A333 |  | 2018-10-26
2018-10-04 | Specification |  | ASTM A350 |  | 2018-10-26
2018-10-04 | Specification |  | ASTM A420 |  | 2018-10-26
2018-10-04 | Coating Type |  | Two-Layer Polyethylene |  | 2018-10-26
2018-10-04 | Feature |  | Strainer |  | 2018-10-26
2018-10-04 | Feature Type |  | Under Strainer: add Other and Unknown |  | 2018-10-26
2018-10-04 | Record Matrix |  |  | Pipe Manufactured year | 2018-10-26
2018-10-04 | Record Matrix |  | Need to update new TVC record pairs
2018-10-04 | Record Matrix |  | Any record (doc type 1) paired with Stand Alone Record_Quality Record (doc type 2) is considered TVC
2018-10-04 | Record Matrix |  | Rated Fittings (Valve, Flange…) require minimum 1 record of any doc type for TVC. Refer to row #29
2018-10-04 | Length Lookup |  | Update length lookup method and half length lookup method
2018-10-05 | Record Matrix |  | Weld Map/Detail and MTR record pair for OD, WT, and Seam Weld
2018-10-11 | Grade |  | WPL6, WPL9
2018-10-11 | Grade |  | Grade 1, Grade 3, Grade 6
2018-10-11 | Feature |  | Joint
2018-10-11 | Feature Type |  | Under Joint: add Insulating, Other and Unknown
2018-10-12 | Feature Length (feet) |  | Move column next to and on the right side of Feature Number column
2018-10-15 | Seam Type |  | "EFW/Seamless"
2018-10-15 | Seam Type |  | "Seamless (Fitting)" [Note: This will default the forged fitting to joint factor = 1 and record matrix check for seam type = Yes even without any record identifier]
2018-10-17 | DP TVC |  | For Pipe and Non-Rated Fittings: Yes for 4 yes record matrix checks, otherwise No. For Rated Fittings: it's a copy of Rating Class Matrix Check column
2018-10-17 | Rating Class Matrix Check |  | At least one record is “Yes”, otherwise No
2018-10-17 | HT TVC |  | "Yes" for non-zero values of PT Min Test Pressure column, otherwise No
2018-10-17 | DP and HT TVC |  | "Yes" for both Yes in DP TVC and HT TVC, otherwise No
2018-10-17 | Governing MAOP |  | The smaller value of (a)(1) and (a)(2) and round up to the next integer value. Example: 1584.91 to 1585
2018-10-17 | Fitting (Rated) |  | Check: for rated fittings, SMYS, Design Factor, and Joint Factor should default to None, Nul…basically no lookup or entered data because there are none.
2018-10-17 | Summary Tables |  | Need to automate the summary tables
2018-10-22 | Feature |  | Add Scrubber |  | 2018-10-26
2018-10-22 | Feature Type |  | Under Scrubber: add Gas, Other and Unknown |  | 2018-10-26
2018-10-22 | Feature |  | Dust Receiver |  | 2018-10-26
2018-10-22 | Feature Type |  | Under Dust Receiver: add Other and Unknown |  | 2018-10-26
2018-10-22 | MFR |  | Aerotec |  | 2018-10-26
2018-10-23 | Doc Type |  | Add Doc Type to build/QC screen
2018-10-24 | Feature |  | Manifold
2018-10-24 | Feature Type |  | Under Manifold: add Forged, Other and Unknown
2018-10-24 | Record Matrix |  | Add 'Blank' Doc Type
2018-10-29 | Record Matrix |  | Color for Matrix Check: Yes = Green, No = Red
2018-10-29 | MFR |  | Cameron, Fisher |  | 2018-10-29
2018-10-29 | Current Class Loc |  |  | None
2018-10-30 | All data fields |  |  | None
2018-10-30 | Rating Class |  | WOG 175
2018-10-31 | Regulator Feature Type |  | Fisher | 399 Fisher, 627 Fisher

## Length LookUp
Feature | Length Lookup |  | Valve (FEET)
Valve | Rating Class 150 LB (285 psi) |  | Outside Diameter | Rating Class 150 LB (285 psi) | Rating Class 300 LB (740 psi) | Rating Class 400 LB (990 psi) | Rating Class 600 LB (1480 psi) | Rating Class 900 LB (2220 psi) | Rating Class 1500 LB (3705 psi) | Rating Class 2500 LB (6170 psi) | Less than Rating Class 150 LB (285 psi) | Greater than Rating Class 2500 LB (6170 psi) | Unknown Rating Class
Relief Valve | Rating Class 300 LB (740 psi) | 0.5 | 0.84 | 0.35417 | 0.4375 | 0.52083 | 0.5625 | 0.70833 | 0.89583 | 0.91667 | 0.35417 | 0.91667 | 0.35417
| Rating Class 400 LB (990 psi) | 0.75 | 1.05 | 0.35417 | 0.47917 | 0.5625 | 0.60417 | 0.77083 | 0.95833 | 1 | 0.35417 | 1 | 0.35417
| Rating Class 600 LB (1480 psi) | 1 | 1.315 | 0.45833 | 0.52083 | 0.58333 | 0.70833 | 0.83333 | 1.0208 | 1.0833 | 0.45833 | 1.0833 | 0.45833
| Rating Class 900 LB (2220 psi) | 1.25 | 1.66 | 0.45833 | 0.57333 | 0.64583 | 0.77083 | 0.89583 | 1.0833 | 1.1825 | 0.45833 | 1.1825 | 0.45833
| Rating Class 1500 LB (3705 psi) | 1.5 | 1.9 | 0.54167 | 0.625 | 0.70833 | 0.83333 | 0.95833 | 1.1458 | 1.2817 | 0.54167 | 1.2817 | 0.54167
| Rating Class 2500 LB (6170 psi) | 2 | 2.375 | 0.58333 | 0.70833 | 0.79167 | 0.95833 | 1.125 | 1.2083 | 1.4792 | 0.58333 | 1.4792 | 0.58333
| Less than Rating Class 150 LB (285 psi) | 2.5 | 2.875 | 0.625 | 0.79167 | 1 | 1.0625 | 1.2292 | 1.375 | 1.7608 | 0.625 | 1.7608 | 0.625
| Greater than Rating Class 2500 LB (6170 psi) | 3 | 3.5 | 0.66667 | 0.92708 | 1.125 | 1.1667 | 1.25 | 1.5417 | 1.8958 | 0.66667 | 1.8958 | 0.66667
| Unknown Rating Class | 3.5 | 4 | 0.70833 | 0.96417 | 1.25 | 1.2917 | 1.375 | 1.6667 | 2.0525 | 0.70833 | 2.0525 | 0.70833
|  | 4 | 4.5 | 0.75 | 1 | 1.3333 | 1.4167 | 1.5 | 1.7917 | 2.2083 | 0.75 | 2.2083 | 0.75
|  | 5 | 5.563 | 1 | 1.1617 | 1.4792 | 1.625 | 1.75 | 2.0525 | 2.6042 | 1 | 2.6042 | 1
|  | 6 | 6.625 | 1.2917 | 1.3229 | 1.625 | 1.8333 | 2 | 2.3125 | 3 | 1.2917 | 3 | 1.2917
|  | 8 | 8.625 | 1.5 | 1.6458 | 1.9583 | 2.1667 | 2.4167 | 2.7292 | 3.375 | 1.5 | 3.375 | 1.5
|  | 10 | 10.75 | 1.75 | 1.8646 | 2.2083 | 2.5833 | 2.75 | 3.25 | 4.1667 | 1.75 | 4.1667 | 1.75
|  | 12 | 12.75 | 2 | 2.125 | 2.5 | 2.75 | 3.1667 | 3.7083 | 4.6667 | 2 | 4.6667 | 2
|  | 14 | 14 | 2.25 | 2.5 | 2.7083 | 2.9167 | 3.375 | 4.125 | 5.0833 | 2.25 | 5.0833 | 2.25
|  | 16 | 16 | 2.5 | 2.75 | 2.9583 | 3.25 | 3.7083 | 4.5417 | 5.5 | 2.5 | 5.5 | 2.5
|  | 18 | 18 | 2.8333 | 3 | 3.2083 | 3.5833 | 4 | 5.0417 | 5.9167 | 2.8333 | 5.9167 | 2.8333
|  | 20 | 20 | 3 | 3.25 | 3.4583 | 3.9167 | 4.3333 | 5.4583 | 6.3333 | 3 | 6.3333 | 3
|  | 22 | 22 | 3.3333 | 3.5833 | 3.75 | 4.25 | 4.7083 | 5.9167 | 6.75 | 3.3333 | 6.75 | 3.3333
|  | 24 | 24 | 3.5 | 3.75 | 4.0417 | 4.5833 | 5.0833 | 6.375 | 7.1667 | 3.5 | 7.1667 | 3.5
|  | 26 | 26 | 3.75 | 4.0833 | 4.5417 | 4.75 | 5.6667 | 6.875 | 7.5833 | 3.75 | 7.5833 | 3.75
|  | 30 | 30 | 4.25 | 4.5833 | 5 | 5.4167 | 6.25 | 7.375 | 8 | 4.25 | 8 | 4.25
|  | 34 | 34 | 4.8333 | 5.3333 | 5.8333 | 6.3333 | 6.875 | 7.875 | 8.4167 | 4.8333 | 8.4167 | 4.8333
|  | 36 | 36 | 5 | 5.6667 | 6.1667 | 6.8333 | 7.5 | 8.3333 | 8.8333 | 5 | 8.8333 | 5
|  | 42 | 42 | 6 | 6.3333 | 6.75 | 6.9167 | 8.3333 | 8.8333 | 9.25 | 6 | 9.25 | 6
Feature | Length Lookup |  | Outside Diameter | 90 Degree_1R (Short Radius) | 90 Degree_1.5R (LR, Long Radius) | 90 Degree_3R | 90 Degree_Unknown Radius | 45 Degree_1R (Short Radius) | 45 Degree_1.5R (LR, Long Radius) | 45 Degree_3R | 45 Degree_Unknown Radius
Elbow | 90 Degree_1R (Short Radius) | 0.5 | 0.84 | 0.06545 | 0.098175 | 0.19635 | 0.06545 | 0.032725 | 0.049087 | 0.098175 | 0.032725
MFG Bend | 90 Degree_1.5R (LR, Long Radius) | 0.75 | 1.05 | 0.098175 | 0.14726 | 0.29452 | 0.098175 | 0.049087 | 0.073631 | 0.14726 | 0.049087
| 90 Degree_3R | 1 | 1.315 | 0.1309 | 0.19635 | 0.3927 | 0.1309 | 0.06545 | 0.098175 | 0.19635 | 0.06545
| 90 Degree_Unknown Radius | 1.25 | 1.66 | 0.16362 | 0.24544 | 0.49087 | 0.16362 | 0.081812 | 0.12272 | 0.24544 | 0.081812
| 45 Degree_1R (Short Radius) | 1.5 | 1.9 | 0.19635 | 0.29452 | 0.58905 | 0.19635 | 0.098175 | 0.14726 | 0.29452 | 0.098175
| 45 Degree_1.5R (LR, Long Radius) | 2 | 2.375 | 0.2618 | 0.3927 | 0.7854 | 0.2618 | 0.1309 | 0.19635 | 0.3927 | 0.1309
| 45 Degree_3R | 2.5 | 2.875 | 0.32725 | 0.49087 | 0.98175 | 0.32725 | 0.16362 | 0.24544 | 0.49087 | 0.16362
| 45 Degree_Unknown Radius | 3 | 3.5 | 0.3927 | 0.58905 | 1.1781 | 0.3927 | 0.19635 | 0.29452 | 0.58905 | 0.19635
|  | 3.5 | 4 | 0.45815 | 0.68722 | 1.3744 | 0.45815 | 0.22907 | 0.34361 | 0.68722 | 0.22907
|  | 4 | 4.5 | 0.5236 | 0.7854 | 1.5708 | 0.5236 | 0.2618 | 0.3927 | 0.7854 | 0.2618
|  | 5 | 5.563 | 0.6545 | 0.98175 | 1.9635 | 0.6545 | 0.32725 | 0.49087 | 0.98175 | 0.32725
|  | 6 | 6.625 | 0.7854 | 1.1781 | 2.3562 | 0.7854 | 0.3927 | 0.58905 | 1.1781 | 0.3927
|  | 8 | 8.625 | 1.0472 | 1.5708 | 3.1416 | 1.0472 | 0.5236 | 0.7854 | 1.5708 | 0.5236
|  | 10 | 10.75 | 1.309 | 1.9635 | 3.927 | 1.309 | 0.6545 | 0.98175 | 1.9635 | 0.6545
|  | 12 | 12.75 | 1.5708 | 2.3562 | 4.7124 | 1.5708 | 0.7854 | 1.1781 | 2.3562 | 0.7854
|  | 14 | 14 | 1.8326 | 2.7489 | 5.4978 | 1.8326 | 0.9163 | 1.3744 | 2.7489 | 0.9163
|  | 16 | 16 | 2.0944 | 3.1416 | 6.2832 | 2.0944 | 1.0472 | 1.5708 | 3.1416 | 1.0472
|  | 18 | 18 | 2.3562 | 3.5343 | 7.0686 | 2.3562 | 1.1781 | 1.7671 | 3.5343 | 1.1781
|  | 20 | 20 | 2.618 | 3.927 | 7.854 | 2.618 | 1.309 | 1.9635 | 3.927 | 1.309
|  | 22 | 22 | 2.8798 | 4.3197 | 8.6394 | 2.8798 | 1.4399 | 2.1598 | 4.3197 | 1.4399
|  | 24 | 24 | 3.1416 | 4.7124 | 9.4248 | 3.1416 | 1.5708 | 2.3562 | 4.7124 | 1.5708
|  | 26 | 26 | 3.4034 | 5.1051 | 10.2102 | 3.4034 | 1.7017 | 2.5525 | 5.1051 | 1.7017
|  | 30 | 30 | 3.927 | 5.8905 | 11.781 | 3.927 | 1.9635 | 2.9452 | 5.8905 | 1.9635
|  | 34 | 34 | 4.4506 | 6.6759 | 13.3518 | 4.4506 | 2.2253 | 3.3379 | 6.6759 | 2.2253
|  | 36 | 36 | 4.7124 | 7.0686 | 14.1372 | 4.7124 | 2.3562 | 3.5343 | 7.0686 | 2.3562
|  | 42 | 42 | 5.4978 | 8.2467 | 16.4933 | 5.4978 | 2.7489 | 4.1233 | 8.2467 | 2.7489
Feature | Length Lookup |  | Outside Diameter | Run Length_Straight or Reducing | Branch Length_Straight Tee | Branch Length_Reducing Tee
Tee | Run Length_Straight or Reducing Tee | 0.5 | 0.84 | 0.16667 | 0.083333 | 0.083333
| Branch Length_Straight Tee | 0.75 | 1.05 | 0.18833 | 0.094167 | 0.094167
| Branch Length_Reducing Tee | 1 | 1.315 | 0.25 | 0.125 | 0.125
|  | 1.25 | 1.66 | 0.31333 | 0.15667 | 0.15667
|  | 1.5 | 1.9 | 0.375 | 0.1875 | 0.1875
|  | 2 | 2.375 | 0.41667 | 0.20833 | 0.175
|  | 2.5 | 2.875 | 0.5 | 0.25 | 0.21104
|  | 3 | 3.5 | 0.56333 | 0.28167 | 0.2475
|  | 3.5 | 4 | 0.625 | 0.3125 | 0.28146
|  | 4 | 4.5 | 0.68833 | 0.34417 | 0.3085
|  | 5 | 5.563 | 0.81333 | 0.40667 | 0.36483
|  | 6 | 6.625 | 0.93833 | 0.46917 | 0.419
|  | 8 | 8.625 | 1.1667 | 0.58333 | 0.52375
|  | 10 | 10.75 | 1.4167 | 0.70833 | 0.63292
|  | 12 | 12.75 | 1.6667 | 0.83333 | 0.74229
|  | 14 | 14 | 1.8333 | 0.91667 | 0.83104
|  | 16 | 16 | 2 | 1 | 0.9315
|  | 18 | 18 | 2.25 | 1.125 | 1.0418
|  | 20 | 20 | 2.5 | 1.25 | 1.139
|  | 22 | 22 | 2.75 | 1.375 | 1.2536
|  | 24 | 24 | 2.8333 | 1.4167 | 1.3508
|  | 26 | 26 | 3.25 | 1.625 | 1.4718
|  | 30 | 30 | 3.6667 | 1.8333 | 1.6417
|  | 34 | 34 | 4.1667 | 2.0833 | 1.9028
|  | 36 | 36 | 4.4167 | 2.2083 | 1.9417
|  | 42 | 42 | 5 | 2.5 | 2.2667
Feature | Length Lookup |  | Outside Diameter | Length_Concentric and Eccentric
Reducer |  | 0.75 | 1.05 | 0.125
|  | 1 | 1.315 | 0.16667
|  | 1.25 | 1.66 | 0.16667
|  | 1.5 | 1.9 | 0.20833
|  | 2 | 2.375 | 0.25
|  | 2.5 | 2.875 | 0.29167
|  | 3 | 3.5 | 0.29167
|  | 3.5 | 4 | 0.33333
|  | 4 | 4.5 | 0.33333
|  | 5 | 5.563 | 0.41667
|  | 6 | 6.625 | 0.45833
|  | 8 | 8.625 | 0.5
|  | 10 | 10.75 | 0.58333
|  | 12 | 12.75 | 0.66667
|  | 14 | 14 | 1.0833
|  | 16 | 16 | 1.1667
|  | 18 | 18 | 1.25
|  | 20 | 20 | 1.6667
|  | 22 | 22 | 1.6667
|  | 24 | 24 | 1.6667
|  | 26 | 26 | 2
|  | 30 | 30 | 2
|  | 34 | 34 | 2
|  | 36 | 36 | 2
|  | 42 | 42 | 2
Feature | Length Lookup |  | Outside Diameter | Length_Cap
Cap |  | 0.5 | 0.84 | 0.083333
|  | 0.75 | 1.05 | 0.083333
|  | 1 | 1.315 | 0.125
|  | 1.25 | 1.66 | 0.125
|  | 1.5 | 1.9 | 0.125
|  | 2 | 2.375 | 0.125
|  | 2.5 | 2.875 | 0.125
|  | 3 | 3.5 | 0.16667
|  | 3.5 | 4 | 0.20833
|  | 4 | 4.5 | 0.20833
|  | 5 | 5.563 | 0.25
|  | 6 | 6.625 | 0.29167
|  | 8 | 8.625 | 0.33333
|  | 10 | 10.75 | 0.41667
|  | 12 | 12.75 | 0.5
|  | 14 | 14 | 0.54167
|  | 16 | 16 | 0.58333
|  | 18 | 18 | 0.66667
|  | 20 | 20 | 0.75
|  | 22 | 22 | 0.83333
|  | 24 | 24 | 0.875
|  | 26 | 26 | 0.875
|  | 30 | 30 | 0.875
|  | 34 | 34 | 0.875
|  | 36 | 36 | 0.875
|  | 42 | 42 | 1
Feature | Length Lookup |  | Outside Diameter | Length_Cross
Cross |  | 1.25 | 1.66 | 0.15667
|  | 1.5 | 1.9 | 0.1875
|  | 2 | 2.375 | 0.20833
|  | 2.5 | 2.875 | 0.25
|  | 3 | 3.5 | 0.28167
|  | 3.5 | 4 | 0.3125
|  | 4 | 4.5 | 0.34417
|  | 5 | 5.563 | 0.40667
|  | 6 | 6.625 | 0.46917
|  | 8 | 8.625 | 0.58333
|  | 10 | 10.75 | 0.70833
|  | 12 | 12.75 | 0.83333
|  | 14 | 14 | 0.91667
|  | 16 | 16 | 1
|  | 18 | 18 | 1.125
|  | 20 | 20 | 1.25
|  | 22 | 22 | 1.375
|  | 24 | 24 | 1.4167
|  | 26 | 26 | 1.625
|  | 30 | 30 | 1.8333
|  | 34 | 34 | 2.0833
Feature | Length Lookup |  | Weld Neck (FEET) | [10 empty] | Slip-On, Threaded, and Socket (FEET) | [9 empty] | Lap Joint (FEET) | [9 empty] | Blind (FEET) | [9 empty] | Unknown (FEET)
Flange | Weld Neck_150 LB |  | Outside Diameter | Weld Neck_150 LB | Weld Neck_300 LB | Weld Neck_400 LB | Weld Neck_600 LB | Weld Neck_900 LB | Weld Neck_1500 LB | Weld Neck_2500 LB | Weld Neck_Unknown Rating |  |  | Outside Diameter | Slip-On, Threaded, and Socket_150 LB | Slip-On, Threaded, and Socket_300 LB | Slip-On, Threaded, and Socket_400 LB | Slip-On, Threaded, and Socket_600 LB | Slip-On, Threaded, and Socket_900 LB | Slip-On, Threaded, and Socket_1500 LB | Slip-On, Threaded, and Socket_2500 LB | Slip-On, Threaded, and Socket_Unknown Rating |  | Outside Diameter | Lap Joint_150 LB | Lap Joint_300 LB | Lap Joint_400 LB | Lap Joint_600 LB | Lap Joint_900 LB | Lap Joint_1500 LB | Lap Joint_2500 LB | Lap Joint_Unknown Rating |  | Outside Diameter | Blind_150 LB | Blind_300 LB | Blind_400 LB | Blind_600 LB | Blind_900 LB | Blind_1500 LB | Blind_2500 LB | Blind_Unknown Rating |  | Outside Diameter | Unknown Flange Type_150 LB | Unknown Flange Type_300 LB | Unknown Flange Type_400 LB | Unknown Flange Type_600 LB | Unknown Flange Type_900 LB | Unknown Flange Type_1500 LB | Unknown Flange Type_2500 LB | Unknown Flange Type_Unknown Rating
| Weld Neck_300 LB | 0.5 | 0.84 | 0.15667 | 0.17167 | 0.17167 | 0.17167 | 0.19833 | 0.19833 | 0.24 | 0.15667 |  | 0.125 | 0.405 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.5 | 0.84 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.5 | 0.84 | 0.036667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.036667 | 0.5 | 0.84 | 0.15667 | 0.17167 | 0.17167 | 0.17167 | 0.19833 | 0.19833 | 0.24 | 0.15667
| Weld Neck_400 LB | 0.75 | 1.05 | 0.17167 | 0.1875 | 0.1875 | 0.1875 | 0.22917 | 0.22917 | 0.26083 | 0.17167 |  | 0.25 | 0.54 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.75 | 1.05 | 0.0525 | 0.083333 | 0.083333 | 0.083333 | 0.115 | 0.115 | 0.14083 | 0.0525 | 0.75 | 1.05 | 0.041667 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.041667 | 0.75 | 1.05 | 0.17167 | 0.1875 | 0.1875 | 0.1875 | 0.22917 | 0.22917 | 0.26083 | 0.17167
| Weld Neck_600 LB | 1 | 1.315 | 0.1825 | 0.20333 | 0.20333 | 0.20333 | 0.24 | 0.24 | 0.29167 | 0.1825 |  | 0.5 | 0.84 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 1 | 1.315 | 0.0575 | 0.088333 | 0.088333 | 0.088333 | 0.13583 | 0.13583 | 0.15667 | 0.0575 | 1 | 1.315 | 0.046667 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.046667 | 1 | 1.315 | 0.1825 | 0.20333 | 0.20333 | 0.20333 | 0.24 | 0.24 | 0.29167 | 0.1825
| Weld Neck_900 LB | 1.25 | 1.66 | 0.1875 | 0.21333 | 0.21917 | 0.21917 | 0.24 | 0.24 | 0.3125 | 0.1875 |  | 0.75 | 1.05 | 0.0525 | 0.083333 | 0.083333 | 0.083333 | 0.115 | 0.115 | 0.14083 | 0.0525 | 1.25 | 1.66 | 0.0675 | 0.088333 | 0.094167 | 0.094167 | 0.13583 | 0.13583 | 0.17167 | 0.0675 | 1.25 | 1.66 | 0.0525 | 0.0625 | 0.0675 | 0.0675 | 0.0675 | 0.0675 | 0.0675 | 0.0525 | 1.25 | 1.66 | 0.1875 | 0.21333 | 0.21917 | 0.21917 | 0.24 | 0.24 | 0.3125 | 0.1875
| Weld Neck_1500 LB | 1.5 | 1.9 | 0.20333 | 0.22417 | 0.22917 | 0.22917 | 0.27083 | 0.27083 | 0.365 | 0.20333 |  | 1 | 1.315 | 0.0575 | 0.088333 | 0.088333 | 0.088333 | 0.13583 | 0.13583 | 0.15667 | 0.0575 | 1.5 | 1.9 | 0.073333 | 0.099167 | 0.10417 | 0.10417 | 0.14583 | 0.14583 | 0.19833 | 0.073333 | 1.5 | 1.9 | 0.0575 | 0.0675 | 0.073333 | 0.073333 | 0.073333 | 0.073333 | 0.073333 | 0.0575 | 1.5 | 1.9 | 0.20333 | 0.22417 | 0.22917 | 0.22917 | 0.27083 | 0.27083 | 0.365 | 0.20333
| Weld Neck_2500 LB | 2 | 2.375 | 0.20833 | 0.22917 | 0.24 | 0.24 | 0.33333 | 0.33333 | 0.41667 | 0.20833 |  | 1.25 | 1.66 | 0.0675 | 0.088333 | 0.094167 | 0.094167 | 0.13583 | 0.13583 | 0.17167 | 0.0675 | 2 | 2.375 | 0.083333 | 0.10917 | 0.12 | 0.12 | 0.1875 | 0.1875 | 0.22917 | 0.083333 | 2 | 2.375 | 0.0625 | 0.073333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.0625 | 2 | 2.375 | 0.20833 | 0.22917 | 0.24 | 0.24 | 0.33333 | 0.33333 | 0.41667 | 0.20833
| Weld Neck_Unknown Rating | 2.5 | 2.875 | 0.22917 | 0.25 | 0.26083 | 0.26083 | 0.34417 | 0.34417 | 0.46917 | 0.22917 |  | 1.5 | 1.9 | 0.073333 | 0.099167 | 0.10417 | 0.10417 | 0.14583 | 0.14583 | 0.19833 | 0.073333 | 2.5 | 2.875 | 0.094167 | 0.125 | 0.13583 | 0.13583 | 0.20833 | 0.20833 | 0.26083 | 0.094167 | 2.5 | 2.875 | 0.073333 | 0.083333 | 0.094167 | 0.094167 | 0.094167 | 0.094167 | 0.094167 | 0.073333 | 2.5 | 2.875 | 0.22917 | 0.25 | 0.26083 | 0.26083 | 0.34417 | 0.34417 | 0.46917 | 0.22917
| Slip-On, Threaded, and Socket_150 LB | 3 | 3.5 | 0.22917 | 0.26083 | 0.27083 | 0.27083 | 0.33333 | 0.38583 | 0.5525 | 0.22917 |  | 2 | 2.375 | 0.083333 | 0.10917 | 0.12 | 0.12 | 0.1875 | 0.1875 | 0.22917 | 0.083333 | 3 | 3.5 | 0.099167 | 0.14083 | 0.15083 | 0.15083 | 0.1775 | 0.24 | 0.3025 | 0.099167 | 3 | 3.5 | 0.078333 | 0.094167 | 0.10417 | 0.10417 | 0.10417 | 0.10417 | 0.10417 | 0.078333 | 3 | 3.5 | 0.22917 | 0.26083 | 0.27083 | 0.27083 | 0.33333 | 0.38583 | 0.5525 | 0.22917
| Slip-On, Threaded, and Socket_300 LB | 3.5 | 4 | 0.23417 | 0.26583 | 0.28167 | 0.28167 | 0.33333 | 0.38583 | 0.58917 | 0.23417 |  | 2.5 | 2.875 | 0.094167 | 0.125 | 0.13583 | 0.13583 | 0.20833 | 0.20833 | 0.26083 | 0.094167 | 3.5 | 4 | 0.10417 | 0.14583 | 0.16167 | 0.16167 | 0.1775 | 0.24 | 0.32833 | 0.10417 | 3.5 | 4 | 0.078333 | 0.099167 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.078333 | 3.5 | 4 | 0.23417 | 0.26583 | 0.28167 | 0.28167 | 0.33333 | 0.38583 | 0.58917 | 0.23417
| Slip-On, Threaded, and Socket_400 LB | 4 | 4.5 | 0.25 | 0.28167 | 0.29167 | 0.33333 | 0.375 | 0.40667 | 0.625 | 0.25 |  | 3 | 3.5 | 0.099167 | 0.14083 | 0.15083 | 0.15083 | 0.1775 | 0.24 | 0.3025 | 0.099167 | 4 | 4.5 | 0.10917 | 0.15667 | 0.16667 | 0.1775 | 0.22917 | 0.29667 | 0.35417 | 0.10917 | 4 | 4.5 | 0.078333 | 0.10417 | 0.115 | 0.125 | 0.125 | 0.125 | 0.125 | 0.078333 | 4 | 4.5 | 0.25 | 0.28167 | 0.29167 | 0.33333 | 0.375 | 0.40667 | 0.625 | 0.25
| Slip-On, Threaded, and Socket_600 LB | 5 | 5.563 | 0.29167 | 0.32333 | 0.33333 | 0.375 | 0.41667 | 0.51083 | 0.75 | 0.29167 |  | 3.5 | 4 | 0.10417 | 0.14583 | 0.16167 | 0.16167 | 0.1775 | 0.24 | 0.32833 | 0.10417 | 5 | 5.563 | 0.12 | 0.16667 | 0.1775 | 0.19833 | 0.26083 | 0.34417 | 0.4275 | 0.12 | 5 | 5.563 | 0.078333 | 0.115 | 0.125 | 0.14583 | 0.14583 | 0.14583 | 0.14583 | 0.078333 | 5 | 5.563 | 0.29167 | 0.32333 | 0.33333 | 0.375 | 0.41667 | 0.51083 | 0.75 | 0.29167
| Slip-On, Threaded, and Socket_900 LB | 6 | 6.625 | 0.29167 | 0.32333 | 0.33833 | 0.38583 | 0.45833 | 0.5625 | 0.89583 | 0.29167 |  | 4 | 4.5 | 0.10917 | 0.15667 | 0.16667 | 0.1775 | 0.22917 | 0.29667 | 0.35417 | 0.10917 | 6 | 6.625 | 0.13 | 0.17167 | 0.1875 | 0.21917 | 0.28167 | 0.39083 | 0.5 | 0.13 | 6 | 6.625 | 0.083333 | 0.12 | 0.13583 | 0.15667 | 0.15667 | 0.15667 | 0.15667 | 0.083333 | 6 | 6.625 | 0.29167 | 0.32333 | 0.33833 | 0.38583 | 0.45833 | 0.5625 | 0.89583 | 0.29167
| Slip-On, Threaded, and Socket_1500 LB | 8 | 8.625 | 0.33333 | 0.365 | 0.38583 | 0.4375 | 0.53167 | 0.69833 | 1.0417 | 0.33333 |  | 5 | 5.563 | 0.12 | 0.16667 | 0.1775 | 0.19833 | 0.26083 | 0.34417 | 0.4275 | 0.12 | 8 | 8.625 | 0.14583 | 0.20333 | 0.22417 | 0.25 | 0.375 | 0.46917 | 0.58333 | 0.14583 | 8 | 8.625 | 0.094167 | 0.13583 | 0.15667 | 0.1825 | 0.1825 | 0.1825 | 0.1825 | 0.094167 | 8 | 8.625 | 0.33333 | 0.365 | 0.38583 | 0.4375 | 0.53167 | 0.69833 | 1.0417 | 0.33333
| Slip-On, Threaded, and Socket_2500 LB | 10 | 10.75 | 0.33333 | 0.38583 | 0.40667 | 0.5 | 0.60417 | 0.83333 | 1.375 | 0.33333 |  | 6 | 6.625 | 0.13 | 0.17167 | 0.1875 | 0.21917 | 0.28167 | 0.39083 | 0.5 | 0.13 | 10 | 10.75 | 0.16167 | 0.3125 | 0.33333 | 0.365 | 0.41667 | 0.58333 | 0.75 | 0.16167 | 10 | 10.75 | 0.099167 | 0.15667 | 0.1775 | 0.20833 | 0.20833 | 0.20833 | 0.20833 | 0.099167 | 10 | 10.75 | 0.33333 | 0.38583 | 0.40667 | 0.5 | 0.60417 | 0.83333 | 1.375 | 0.33333
| Slip-On, Threaded, and Socket_Unknown Rating | 12 | 12.75 | 0.375 | 0.4275 | 0.44833 | 0.51083 | 0.65667 | 0.9275 | 1.5208 | 0.375 |  | 8 | 8.625 | 0.14583 | 0.20333 | 0.22417 | 0.25 | 0.33333 | 0.46917 | 0.58333 | 0.14583 | 12 | 12.75 | 0.1825 | 0.33333 | 0.35417 | 0.38583 | 0.46917 | 0.71917 | 0.83333 | 0.1825 | 12 | 12.75 | 0.10417 | 0.16667 | 0.1875 | 0.21917 | 0.21917 | 0.21917 | 0.21917 | 0.10417 | 12 | 12.75 | 0.375 | 0.4275 | 0.44833 | 0.51083 | 0.65667 | 0.9275 | 1.5208 | 0.375
| Lap Joint_150 LB | 14 | 14 | 0.41667 | 0.46917 | 0.49 | 0.54167 | 0.69833 | 0.97917 | 1.5833 | 0.41667 |  | 10 | 10.75 | 0.16167 | 0.21917 | 0.24 | 0.28167 | 0.35417 | 0.52083 | 0.75 | 0.16167 | 14 | 14 | 0.26083 | 0.365 | 0.38583 | 0.41667 | 0.51083 | 0.79167 | 0.89583 | 0.26083 | 14 | 14 | 0.115 | 0.1775 | 0.19833 | 0.22917 | 0.22917 | 0.22917 | 0.22917 | 0.115 | 14 | 14 | 0.41667 | 0.46917 | 0.49 | 0.54167 | 0.69833 | 0.97917 | 1.5833 | 0.41667
| Lap Joint_300 LB | 16 | 16 | 0.41667 | 0.47917 | 0.5 | 0.58333 | 0.70833 | 1.0208 | 1.6458 | 0.41667 |  | 12 | 12.75 | 0.1825 | 0.24 | 0.26083 | 0.3025 | 0.38583 | 0.59417 | 0.83333 | 0.1825 | 16 | 16 | 0.28667 | 0.39583 | 0.41667 | 0.45833 | 0.54167 | 0.85417 | 0.95833 | 0.28667 | 16 | 16 | 0.12 | 0.1875 | 0.20833 | 0.25 | 0.25 | 0.25 | 0.25 | 0.12 | 16 | 16 | 0.41667 | 0.47917 | 0.5 | 0.58333 | 0.70833 | 1.0208 | 1.6458 | 0.41667
| Lap Joint_400 LB | 18 | 18 | 0.45833 | 0.52083 | 0.54167 | 0.60417 | 0.75 | 1.0733 | 1.7083 | 0.45833 |  | 14 | 14 | 0.1875 | 0.25 | 0.27583 | 0.3075 | 0.4275 | 0.64583 | 0.89583 | 0.1875 | 18 | 18 | 0.26583 | 0.4275 | 0.44833 | 0.5 | 0.625 | 0.90667 | 1.0208 | 0.26583 | 18 | 18 | 0.13 | 0.19833 | 0.21917 | 0.27083 | 0.27083 | 0.27083 | 0.27083 | 0.13 | 18 | 18 | 0.45833 | 0.52083 | 0.54167 | 0.60417 | 0.75 | 1.0733 | 1.7083 | 0.45833
| Lap Joint_600 LB | 20 | 20 | 0.47417 | 0.53167 | 0.5525 | 0.625 | 0.8125 | 1.1667 | 1.7708 | 0.47417 |  | 16 | 16 | 0.20833 | 0.27083 | 0.3075 | 0.34917 | 0.4375 | 0.70833 | 0.95833 | 0.20833 | 20 | 20 | 0.33833 | 0.45833 | 0.47917 | 0.54167 | 0.6875 | 0.95833 | 1.0833 | 0.33833 | 20 | 20 | 0.14083 | 0.20833 | 0.22917 | 0.29167 | 0.29167 | 0.29167 | 0.29167 | 0.14083 | 20 | 20 | 0.47417 | 0.53167 | 0.5525 | 0.625 | 0.8125 | 1.1667 | 1.7708 | 0.47417
| Lap Joint_900 LB | 22 | 22 | 0.49 | 0.54167 | 0.5625 | 0.64583 | 0.88583 | 1.25 | 1.8333 | 0.49 |  | 18 | 18 | 0.22417 | 0.29167 | 0.32333 | 0.38583 | 0.5 | 0.77083 | 1.0208 | 0.22417 | 24 | 24 | 0.365 | 0.5 | 0.52083 | 0.60417 | 0.875 | 1.0833 | 1.1458 | 0.365 | 22 | 22 | 0.15083 | 0.21917 | 0.24 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.15083 | 22 | 22 | 0.49 | 0.54167 | 0.5625 | 0.64583 | 0.88583 | 1.25 | 1.8333 | 0.49
| Lap Joint_1500 LB | 24 | 24 | 0.5 | 0.5525 | 0.57333 | 0.66667 | 0.95833 | 1.3333 | 1.8958 | 0.5 |  | 20 | 20 | 0.24 | 0.3125 | 0.33333 | 0.41667 | 0.52083 | 0.83333 | 1.0833 | 0.24 | [10 empty] | 24 | 24 | 0.15667 | 0.22917 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.15667 | 24 | 24 | 0.5 | 0.5525 | 0.57333 | 0.66667 | 0.95833 | 1.3333 | 1.8958 | 0.5
| Lap Joint_2500 LB | 26 | 26 | 0.41667 | 0.60417 | 0.63583 | 0.72917 | 1.0208 | 1.4167 | 1.9583 | 0.41667 |  | 22 | 22 | 0.26083 | 0.33333 | 0.35417 | 0.4375 | 0.59417 | 0.89583 | 1.1458 | 0.26083 | [10 empty] | 26 | 26 | 0.16667 | 0.26083 | 0.29167 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.16667 | 26 | 26 | 0.41667 | 0.60417 | 0.63583 | 0.72917 | 1.0208 | 1.4167 | 1.9583 | 0.41667
| Lap Joint_Unknown Rating | 30 | 30 | 0.4275 | 0.6875 | 0.71917 | 0.79167 | 1.0833 | 1.5 | 2.0208 | 0.4275 |  | 24 | 24 | 0.27083 | 0.34917 | 0.375 | 0.45833 | 0.66667 | 0.95833 | 1.2083 | 0.27083 | [10 empty] | 30 | 30 | 0.1775 | 0.3025 | 0.33333 | 0.375 | 0.375 | 0.375 | 0.375 | 0.1775 | 30 | 30 | 0.4275 | 0.6875 | 0.71917 | 0.79167 | 1.0833 | 1.5 | 2.0208 | 0.4275
| Blind_150 LB | 34 | 34 | 0.4425 | 0.76083 | 0.79167 | 0.85417 | 1.1458 | 1.5833 | 2.0833 | 0.4425 |  | 26 | 26 | 0.28167 | 0.60417 | 0.63583 | 0.72917 | 0.91667 | 1.0208 | 1.2708 | 0.28167 | [10 empty] | 34 | 34 | 0.1925 | 0.33333 | 0.365 | 0.39583 | 0.39583 | 0.39583 | 0.39583 | 0.1925 | 34 | 34 | 0.4425 | 0.76083 | 0.79167 | 0.85417 | 1.1458 | 1.5833 | 2.0833 | 0.4425
| Blind_300 LB | 36 | 36 | 0.44833 | 0.79167 | 0.82333 | 0.91667 | 1.2083 | 1.6667 | 2.1458 | 0.44833 |  | 30 | 30 | 0.29167 | 0.6875 | 0.71917 | 0.8125 | 0.97917 | 1.0833 | 1.3333 | 0.29167 | [10 empty] | 36 | 36 | 0.19833 | 0.34417 | 0.375 | 0.40667 | 0.40667 | 0.40667 | 0.40667 | 0.19833 | 36 | 36 | 0.44833 | 0.79167 | 0.82333 | 0.91667 | 1.2083 | 1.6667 | 2.1458 | 0.44833
| Blind_400 LB | 42 | 42 | 0.46917 | 0.90667 | 0.94833 | 0.97917 | 1.2708 | 1.75 | 2.2083 | 0.46917 |  | 34 | 34 | 0.3075 | 0.76083 | 0.79167 | 0.88583 | 1.0417 | 1.1458 | 1.3958 | 0.3075 | [10 empty] | 42 | 42 | 0.21917 | 0.38583 | 0.4275 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.21917 | 42 | 42 | 0.46917 | 0.90667 | 0.94833 | 0.97917 | 1.2708 | 1.75 | 2.2083 | 0.46917
| Blind_600 LB | [11 empty] | 36 | 36 | 0.3125 | 0.79167 | 0.82333 | 0.9275 | 1.1042 | 1.2083 | 1.4583 | 0.3125
| Blind_900 LB | [11 empty] | 42 | 42 | 0.33333 | 0.90667 | 0.94833 | 1.0625 | 1.1667 | 1.2708 | 1.5208 | 0.33333
Blind_1500 LB
Blind_2500 LB
Blind_Unknown Rating
Unknown_150 LB
Unknown_300 LB
Unknown_400 LB
Unknown_600 LB
Unknown_900 LB
Unknown_1500 LB
Unknown_2500 LB
Unknown_Unknown Rating

## Feature Types (hidden)
Feature Type
Pipe | F | Pipe Type |  | Tap Type | Field Bend Type | Mfg. Bend Type | Tee Type | Valve Type | Reducer Type | Sleeve Type | PCF Type | Flange Type | Meter Type | Regulator Type | Relief Valve Type | Cap Type
Tap | FT | Casing | FT | Drip-External | Miter | Forged | Straight Tee | Ball | Conc.-Std | Type A | Top Tap | Weld Neck | Turbine | Mooney | Ball Valve | Pipe
Field Bend | FT | No Casing | FT | Drip-Internal | Bell Bell Chill Ring | Miter | Reinforced Tee | Gate | Conc.-Ven | Type B | Side Tap | Blind | Insertion Turbine | Flex Flow | Gate Valve | Other
Mfg Bend | FT | Pipe Bridge | F/CLASS | Insertion Probe | Wrinkle | Bell Bell Chill Ring | Reducing Tee | Plug | ECC-Std | Clockspring | Bottom Tap | Slip On | Insertion Probe | Axial Flow | Control Valve
Tee | FT | Pipe Span | F/CLASS | Thermowell | Bending Machine | Wrinkle | Straight Y | Control Ball | ECC-Ven | Aqua Wrap | Line Stopper | Lap Joint | Sonic | Boot Type | Regulator Valve
Valve | FT | Pipe Liner | REMOVE | Take-off | Int Mandrel-Bending Machine | Rolled Plate | Reducing Y | Check | Internal Only | Half Sleeve | TDW | Threaded | Micrometer | Diaphragm | Block
Reducer | FT | Pipe Encased | REMOVE | Take-off Service Tee | Unknown | Reducing | Cross | Curb Valve Tee w/ nut-Mueller | Other | Patch | Stopple | Reducing | Rotary | Spring | Check Valve
Sleeve | FT |  |  | Take-off Pin off-Valve Tee |  | Socket Weld | Other | Other | Unknown | Repair | Other | Socket Weld | Diaphragm | 399 Fisher | Flex Flow Valve
PCF | ? |  |  | Take-off Curb Valve Tee w/ nut |  | Unknown | Unknown | Unknown |  | PLIDCO - repair clamp | Unknown | Insulating | OrificeSkidMntGasWell | 627 Fisher | Blowdown Valve
Flange | FT |  |  | Connection | [5 empty] | Other |  | Unknown | Orifice | Fire Fuse - Slam Shut | Spring Type
Meter | FT |  |  | Connection Service Tee | [5 empty] | Unknown |  |  | Unknown | Slam shut | Butterfly Valve
Regulator | FT |  |  | Connection Pin off-Valve Tee | [9 empty] | HPR Set | Unknown
Relief Valve | FT |  |  | Connection Curb Valve Tee w/nut | [9 empty] | Other
Cap | FT |  |  | Save-a-valve | [9 empty] | Unknown
Other | REMOVE |  |  | Other
Unknown
The "Feature Type" is the first selection option. The types on Row 2 are the secondary selections that will be populated when chosing the Feature Type.

## Elbow Length
Elbow Length Calculator
Degrees | 90 | Degree of bend
R Factor | 1 | Radius (SR=1, LR=1.5, 3R=3, 5R=5 etc.), typical value for R = 1.5
Outside Diameter | 42 | Nominal Outside Diameter of the pipe, if OD = 4, apply 4, not 4.5
Total Length (ft) | 5.4978
[5 empty] | Degrees | R Factor
|  | Elbow Length = (Degrees/360)*2*3.14159*OD*R |  |  | 45 | 1
[5 empty] | 90 | 1.5
|  | If OD is missing, do not calculate. |  |  |  | 3
Unknown
|  | if R = unknown: default to R = 1.0 |  |  | Elbow Data Type
|  |  |  | Outside Diameter | 90 Degree_1R (Short Radius) | 90 Degree_1.5R (LR, Long Radius) | 90 Degree_3R | 90 Degree_Unknown R | 45 Degree_1R (Short Radius) | 45 Degree_1.5R (LR, Long Radius) | 45 Degree_3R | 45 Degree_Unknown R
|  |  | 0.5 | 0.84 | 0.06545 | 0.098175 | 0.19635 | 0.06545 | 0.032725 | 0.049087 | 0.098175 | 0.032725
|  |  | 0.75 | 1.05 | 0.098175 | 0.14726 | 0.29452 | 0.098175 | 0.049087 | 0.073631 | 0.14726 | 0.049087
|  |  | 1 | 1.315 | 0.1309 | 0.19635 | 0.3927 | 0.1309 | 0.06545 | 0.098175 | 0.19635 | 0.06545
|  |  | 1.25 | 1.66 | 0.16362 | 0.24544 | 0.49087 | 0.16362 | 0.081812 | 0.12272 | 0.24544 | 0.081812
|  |  | 1.5 | 1.9 | 0.19635 | 0.29452 | 0.58905 | 0.19635 | 0.098175 | 0.14726 | 0.29452 | 0.098175
|  |  | 2 | 2.375 | 0.2618 | 0.3927 | 0.7854 | 0.2618 | 0.1309 | 0.19635 | 0.3927 | 0.1309
|  |  | 2.5 | 2.875 | 0.32725 | 0.49087 | 0.98175 | 0.32725 | 0.16362 | 0.24544 | 0.49087 | 0.16362
|  |  | 3 | 3.5 | 0.3927 | 0.58905 | 1.1781 | 0.3927 | 0.19635 | 0.29452 | 0.58905 | 0.19635
|  |  | 3.5 | 4 | 0.45815 | 0.68722 | 1.3744 | 0.45815 | 0.22907 | 0.34361 | 0.68722 | 0.22907
|  |  | 4 | 4.5 | 0.5236 | 0.7854 | 1.5708 | 0.5236 | 0.2618 | 0.3927 | 0.7854 | 0.2618
|  |  | 5 | 5.563 | 0.6545 | 0.98175 | 1.9635 | 0.6545 | 0.32725 | 0.49087 | 0.98175 | 0.32725
|  |  | 6 | 6.625 | 0.7854 | 1.1781 | 2.3562 | 0.7854 | 0.3927 | 0.58905 | 1.1781 | 0.3927
|  |  | 8 | 8.625 | 1.0472 | 1.5708 | 3.1416 | 1.0472 | 0.5236 | 0.7854 | 1.5708 | 0.5236
|  |  | 10 | 10.75 | 1.309 | 1.9635 | 3.927 | 1.309 | 0.6545 | 0.98175 | 1.9635 | 0.6545
|  |  | 12 | 12.75 | 1.5708 | 2.3562 | 4.7124 | 1.5708 | 0.7854 | 1.1781 | 2.3562 | 0.7854
|  |  | 14 | 14 | 1.8326 | 2.7489 | 5.4978 | 1.8326 | 0.9163 | 1.3744 | 2.7489 | 0.9163
|  |  | 16 | 16 | 2.0944 | 3.1416 | 6.2832 | 2.0944 | 1.0472 | 1.5708 | 3.1416 | 1.0472
|  |  | 18 | 18 | 2.3562 | 3.5343 | 7.0686 | 2.3562 | 1.1781 | 1.7671 | 3.5343 | 1.1781
|  |  | 20 | 20 | 2.618 | 3.927 | 7.854 | 2.618 | 1.309 | 1.9635 | 3.927 | 1.309
|  |  | 22 | 22 | 2.8798 | 4.3197 | 8.6394 | 2.8798 | 1.4399 | 2.1598 | 4.3197 | 1.4399
|  |  | 24 | 24 | 3.1416 | 4.7124 | 9.4248 | 3.1416 | 1.5708 | 2.3562 | 4.7124 | 1.5708
|  |  | 26 | 26 | 3.4034 | 5.1051 | 10.2102 | 3.4034 | 1.7017 | 2.5525 | 5.1051 | 1.7017
|  |  | 30 | 30 | 3.927 | 5.8905 | 11.781 | 3.927 | 1.9635 | 2.9452 | 5.8905 | 1.9635
|  |  | 34 | 34 | 4.4506 | 6.6759 | 13.3518 | 4.4506 | 2.2253 | 3.3379 | 6.6759 | 2.2253
|  |  | 36 | 36 | 4.7124 | 7.0686 | 14.1372 | 4.7124 | 2.3562 | 3.5343 | 7.0686 | 2.3562
|  |  | 42 | 42 | 5.4978 | 8.2467 | 16.4933 | 5.4978 | 2.7489 | 4.1233 | 8.2467 | 2.7489
|  |  | Feature | Length Lookup
|  |  | Elbow | 90 Degree_1R (Short Radius)
|  |  | MFG Bend | 90 Degree_1.5R (LR, Long Radius)
90 Degree_3R
90 Degree_Unknown R
45 Degree_1R (Short Radius)
45 Degree_1.5R (LR, Long Radius)
45 Degree_3R
45 Degree_Unknown R

## Flange Length (hidden)
If OD is missing, do not calculate length |  | Flange | Nominal Outside Diameter | Flange Type | Rating Class
|  |  |  | Weld Neck | 150
|  |  |  | Slip On | 300
|  |  |  | Threaded | 400
|  |  |  | Lap Joint | 600
|  |  |  | Blind | 900
If Flange Type = unknown: default to Weld Neck flange type |  |  |  | Unknown | 1500
2500
If Rating = unknown: default to 150 rating |  |  |  |  | Unknown
|  | Weld Neck (INCHES) | [9 empty] | Slip-On, Threaded, and Socket (INCHES) | [9 empty] | Lap Joint (INCHES) | [9 empty] | Blind (INCHES) | [9 empty] | Unknown (INCHES)
|  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB | Unknown Rating |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB | Unknown Rating |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB | Unknown Rating |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB | Unknown Rating |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB | Unknown Rating
| 0.5 | 0.84 | 1.88 | 2.06 | 2.06 | 2.06 | 2.38 | 2.38 | 2.88 | 1.88 | 0.125 | 0.405 | 0.63 | 0.88 | 0.88 | 0.88 | 1.25 | 1.25 | 1.56 | 0.63 | 0.5 | 0.84 | 0.63 | 0.88 | 0.88 | 0.88 | 1.25 | 1.25 | 1.56 | 0.63 | 0.5 | 0.84 | 0.44 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.44 | 0.5 | 0.84 | 1.88 | 2.06 | 2.06 | 2.06 | 2.38 | 2.38 | 2.88 | 1.88
| 0.75 | 1.05 | 2.06 | 2.25 | 2.25 | 2.25 | 2.75 | 2.75 | 3.13 | 2.06 | 0.25 | 0.54 | 0.63 | 0.88 | 0.88 | 0.88 | 1.25 | 1.25 | 1.56 | 0.63 | 0.75 | 1.05 | 0.63 | 1 | 1 | 1 | 1.38 | 1.38 | 1.69 | 0.63 | 0.75 | 1.05 | 0.5 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.5 | 0.75 | 1.05 | 2.06 | 2.25 | 2.25 | 2.25 | 2.75 | 2.75 | 3.13 | 2.06
| 1 | 1.315 | 2.19 | 2.44 | 2.44 | 2.44 | 2.88 | 2.88 | 3.5 | 2.19 | 0.5 | 0.84 | 0.63 | 0.88 | 0.88 | 0.88 | 1.25 | 1.25 | 1.56 | 0.63 | 1 | 1.315 | 0.69 | 1.06 | 1.06 | 1.06 | 1.63 | 1.63 | 1.88 | 0.69 | 1 | 1.315 | 0.56 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.56 | 1 | 1.315 | 2.19 | 2.44 | 2.44 | 2.44 | 2.88 | 2.88 | 3.5 | 2.19
| 1.25 | 1.66 | 2.25 | 2.56 | 2.63 | 2.63 | 2.88 | 2.88 | 3.75 | 2.25 | 0.75 | 1.05 | 0.63 | 1 | 1 | 1 | 1.38 | 1.38 | 1.69 | 0.63 | 1.25 | 1.66 | 0.81 | 1.06 | 1.13 | 1.13 | 1.63 | 1.63 | 2.06 | 0.81 | 1.25 | 1.66 | 0.63 | 0.75 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.63 | 1.25 | 1.66 | 2.25 | 2.56 | 2.63 | 2.63 | 2.88 | 2.88 | 3.75 | 2.25
| 1.5 | 1.9 | 2.44 | 2.69 | 2.75 | 2.75 | 3.25 | 3.25 | 4.38 | 2.44 | 1 | 1.315 | 0.69 | 1.06 | 1.06 | 1.06 | 1.63 | 1.63 | 1.88 | 0.69 | 1.5 | 1.9 | 0.88 | 1.19 | 1.25 | 1.25 | 1.75 | 1.75 | 2.38 | 0.88 | 1.5 | 1.9 | 0.69 | 0.81 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.69 | 1.5 | 1.9 | 2.44 | 2.69 | 2.75 | 2.75 | 3.25 | 3.25 | 4.38 | 2.44
| 2 | 2.375 | 2.5 | 2.75 | 2.88 | 2.88 | 4 | 4 | 5 | 2.5 | 1.25 | 1.66 | 0.81 | 1.06 | 1.13 | 1.13 | 1.63 | 1.63 | 2.06 | 0.81 | 2 | 2.375 | 1 | 1.31 | 1.44 | 1.44 | 2.25 | 2.25 | 2.75 | 1 | 2 | 2.375 | 0.75 | 0.88 | 1 | 1 | 1 | 1 | 1 | 0.75 | 2 | 2.375 | 2.5 | 2.75 | 2.88 | 2.88 | 4 | 4 | 5 | 2.5
| 2.5 | 2.875 | 2.75 | 3 | 3.13 | 3.13 | 4.13 | 4.13 | 5.63 | 2.75 | 1.5 | 1.9 | 0.88 | 1.19 | 1.25 | 1.25 | 1.75 | 1.75 | 2.38 | 0.88 | 2.5 | 2.875 | 1.13 | 1.5 | 1.63 | 1.63 | 2.5 | 2.5 | 3.13 | 1.13 | 2.5 | 2.875 | 0.88 | 1 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 0.88 | 2.5 | 2.875 | 2.75 | 3 | 3.13 | 3.13 | 4.13 | 4.13 | 5.63 | 2.75
| 3 | 3.5 | 2.75 | 3.13 | 3.25 | 3.25 | 4 | 4.63 | 6.63 | 2.75 | 2 | 2.375 | 1 | 1.31 | 1.44 | 1.44 | 2.25 | 2.25 | 2.75 | 1 | 3 | 3.5 | 1.19 | 1.69 | 1.81 | 1.81 | 2.13 | 2.88 | 3.63 | 1.19 | 3 | 3.5 | 0.94 | 1.13 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 0.94 | 3 | 3.5 | 2.75 | 3.13 | 3.25 | 3.25 | 4 | 4.63 | 6.63 | 2.75
| 3.5 | 4 | 2.81 | 3.19 | 3.38 | 3.38 | 4 | 4.63 | 7.07 | 2.81 | 2.5 | 2.875 | 1.13 | 1.5 | 1.63 | 1.63 | 2.5 | 2.5 | 3.13 | 1.13 | 3.5 | 4 | 1.25 | 1.75 | 1.94 | 1.94 | 2.13 | 2.88 | 3.94 | 1.25 | 3.5 | 4 | 0.94 | 1.19 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 0.94 | 3.5 | 4 | 2.81 | 3.19 | 3.38 | 3.38 | 4 | 4.63 | 7.07 | 2.81
| 4 | 4.5 | 3 | 3.38 | 3.5 | 4 | 4.5 | 4.88 | 7.5 | 3 | 3 | 3.5 | 1.19 | 1.69 | 1.81 | 1.81 | 2.13 | 2.88 | 3.63 | 1.19 | 4 | 4.5 | 1.31 | 1.88 | 2 | 2.13 | 2.75 | 3.56 | 4.25 | 1.31 | 4 | 4.5 | 0.94 | 1.25 | 1.38 | 1.5 | 1.5 | 1.5 | 1.5 | 0.94 | 4 | 4.5 | 3 | 3.38 | 3.5 | 4 | 4.5 | 4.88 | 7.5 | 3
| 5 | 5.563 | 3.5 | 3.88 | 4 | 4.5 | 5 | 6.13 | 9 | 3.5 | 3.5 | 4 | 1.25 | 1.75 | 1.94 | 1.94 | 2.13 | 2.88 | 3.94 | 1.25 | 5 | 5.563 | 1.44 | 2 | 2.13 | 2.38 | 3.13 | 4.13 | 5.13 | 1.44 | 5 | 5.563 | 0.94 | 1.38 | 1.5 | 1.75 | 1.75 | 1.75 | 1.75 | 0.94 | 5 | 5.563 | 3.5 | 3.88 | 4 | 4.5 | 5 | 6.13 | 9 | 3.5
| 6 | 6.625 | 3.5 | 3.88 | 4.06 | 4.63 | 5.5 | 6.75 | 10.75 | 3.5 | 4 | 4.5 | 1.31 | 1.88 | 2 | 2.13 | 2.75 | 3.56 | 4.25 | 1.31 | 6 | 6.625 | 1.56 | 2.06 | 2.25 | 2.63 | 3.38 | 4.69 | 6 | 1.56 | 6 | 6.625 | 1 | 1.44 | 1.63 | 1.88 | 1.88 | 1.88 | 1.88 | 1 | 6 | 6.625 | 3.5 | 3.88 | 4.06 | 4.63 | 5.5 | 6.75 | 10.75 | 3.5
| 8 | 8.625 | 4 | 4.38 | 4.63 | 5.25 | 6.38 | 8.38 | 12.5 | 4 | 5 | 5.563 | 1.44 | 2 | 2.13 | 2.38 | 3.13 | 4.13 | 5.13 | 1.44 | 8 | 8.625 | 1.75 | 2.44 | 2.69 | 3 | 4.5 | 5.63 | 7 | 1.75 | 8 | 8.625 | 1.13 | 1.63 | 1.88 | 2.19 | 2.19 | 2.19 | 2.19 | 1.13 | 8 | 8.625 | 4 | 4.38 | 4.63 | 5.25 | 6.38 | 8.38 | 12.5 | 4
| 10 | 10.75 | 4 | 4.63 | 4.88 | 6 | 7.25 | 10 | 16.5 | 4 | 6 | 6.625 | 1.56 | 2.06 | 2.25 | 2.63 | 3.38 | 4.69 | 6 | 1.56 | 10 | 10.75 | 1.94 | 3.75 | 4 | 4.38 | 5 | 7 | 9 | 1.94 | 10 | 10.75 | 1.19 | 1.88 | 2.13 | 2.5 | 2.5 | 2.5 | 2.5 | 1.19 | 10 | 10.75 | 4 | 4.63 | 4.88 | 6 | 7.25 | 10 | 16.5 | 4
| 12 | 12.75 | 4.5 | 5.13 | 5.38 | 6.13 | 7.88 | 11.13 | 18.25 | 4.5 | 8 | 8.625 | 1.75 | 2.44 | 2.69 | 3 | 4 | 5.63 | 7 | 1.75 | 12 | 12.75 | 2.19 | 4 | 4.25 | 4.63 | 5.63 | 8.63 | 10 | 2.19 | 12 | 12.75 | 1.25 | 2 | 2.25 | 2.63 | 2.63 | 2.63 | 2.63 | 1.25 | 12 | 12.75 | 4.5 | 5.13 | 5.38 | 6.13 | 7.88 | 11.13 | 18.25 | 4.5
| 14 | 14 | 5 | 5.63 | 5.88 | 6.5 | 8.38 | 11.75 | 19 | 5 | 10 | 10.75 | 1.94 | 2.63 | 2.88 | 3.38 | 4.25 | 6.25 | 9 | 1.94 | 14 | 14 | 3.13 | 4.38 | 4.63 | 5 | 6.13 | 9.5 | 10.75 | 3.13 | 14 | 14 | 1.38 | 2.13 | 2.38 | 2.75 | 2.75 | 2.75 | 2.75 | 1.38 | 14 | 14 | 5 | 5.63 | 5.88 | 6.5 | 8.38 | 11.75 | 19 | 5
| 16 | 16 | 5 | 5.75 | 6 | 7 | 8.5 | 12.25 | 19.75 | 5 | 12 | 12.75 | 2.19 | 2.88 | 3.13 | 3.63 | 4.63 | 7.13 | 10 | 2.19 | 16 | 16 | 3.44 | 4.75 | 5 | 5.5 | 6.5 | 10.25 | 11.5 | 3.44 | 16 | 16 | 1.44 | 2.25 | 2.5 | 3 | 3 | 3 | 3 | 1.44 | 16 | 16 | 5 | 5.75 | 6 | 7 | 8.5 | 12.25 | 19.75 | 5
| 18 | 18 | 5.5 | 6.25 | 6.5 | 7.25 | 9 | 12.88 | 20.5 | 5.5 | 14 | 14 | 2.25 | 3 | 3.31 | 3.69 | 5.13 | 7.75 | 10.75 | 2.25 | 18 | 18 | 3.19 | 5.13 | 5.38 | 6 | 7.5 | 10.88 | 12.25 | 3.19 | 18 | 18 | 1.56 | 2.38 | 2.63 | 3.25 | 3.25 | 3.25 | 3.25 | 1.56 | 18 | 18 | 5.5 | 6.25 | 6.5 | 7.25 | 9 | 12.88 | 20.5 | 5.5
| 20 | 20 | 5.69 | 6.38 | 6.63 | 7.5 | 9.75 | 14 | 21.25 | 5.69 | 16 | 16 | 2.5 | 3.25 | 3.69 | 4.19 | 5.25 | 8.5 | 11.5 | 2.5 | 20 | 20 | 4.06 | 5.5 | 5.75 | 6.5 | 8.25 | 11.5 | 13 | 4.06 | 20 | 20 | 1.69 | 2.5 | 2.75 | 3.5 | 3.5 | 3.5 | 3.5 | 1.69 | 20 | 20 | 5.69 | 6.38 | 6.63 | 7.5 | 9.75 | 14 | 21.25 | 5.69
| 22 | 22 | 5.88 | 6.5 | 6.75 | 7.75 | 10.63 | 15 | 22 | 5.88 | 18 | 18 | 2.69 | 3.5 | 3.88 | 4.63 | 6 | 9.25 | 12.25 | 2.69 | 24 | 24 | 4.38 | 6 | 6.25 | 7.25 | 10.5 | 13 | 13.75 | 4.38 | 22 | 22 | 1.81 | 2.63 | 2.88 | 3.75 | 3.75 | 3.75 | 3.75 | 1.81 | 22 | 22 | 5.88 | 6.5 | 6.75 | 7.75 | 10.63 | 15 | 22 | 5.88
| 24 | 24 | 6 | 6.63 | 6.88 | 8 | 11.5 | 16 | 22.75 | 6 | 20 | 20 | 2.88 | 3.75 | 4 | 5 | 6.25 | 10 | 13 | 2.88 | [10 empty] | 24 | 24 | 1.88 | 2.75 | 3 | 4 | 4 | 4 | 4 | 1.88 | 24 | 24 | 6 | 6.63 | 6.88 | 8 | 11.5 | 16 | 22.75 | 6
| 26 | 26 | 5 | 7.25 | 7.63 | 8.75 | 12.25 | 17 | 23.5 | 5 | 22 | 22 | 3.13 | 4 | 4.25 | 5.25 | 7.13 | 10.75 | 13.75 | 3.13 | [10 empty] | 26 | 26 | 2 | 3.13 | 3.5 | 4.25 | 4.25 | 4.25 | 4.25 | 2 | 26 | 26 | 5 | 7.25 | 7.63 | 8.75 | 12.25 | 17 | 23.5 | 5
| 30 | 30 | 5.13 | 8.25 | 8.63 | 9.5 | 13 | 18 | 24.25 | 5.13 | 24 | 24 | 3.25 | 4.19 | 4.5 | 5.5 | 8 | 11.5 | 14.5 | 3.25 | [10 empty] | 30 | 30 | 2.13 | 3.63 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 2.13 | 30 | 30 | 5.13 | 8.25 | 8.63 | 9.5 | 13 | 18 | 24.25 | 5.13
| 34 | 34 | 5.31 | 9.13 | 9.5 | 10.25 | 13.75 | 19 | 25 | 5.31 | 26 | 26 | 3.38 | 7.25 | 7.63 | 8.75 | 11 | 12.25 | 15.25 | 3.38 | [10 empty] | 34 | 34 | 2.31 | 4 | 4.38 | 4.75 | 4.75 | 4.75 | 4.75 | 2.31 | 34 | 34 | 5.31 | 9.13 | 9.5 | 10.25 | 13.75 | 19 | 25 | 5.31
| 36 | 36 | 5.38 | 9.5 | 9.88 | 11 | 14.5 | 20 | 25.75 | 5.38 | 30 | 30 | 3.5 | 8.25 | 8.63 | 9.75 | 11.75 | 13 | 16 | 3.5 | [10 empty] | 36 | 36 | 2.38 | 4.13 | 4.5 | 4.88 | 4.88 | 4.88 | 4.88 | 2.38 | 36 | 36 | 5.38 | 9.5 | 9.88 | 11 | 14.5 | 20 | 25.75 | 5.38
| 42 | 42 | 5.63 | 10.88 | 11.38 | 11.75 | 15.25 | 21 | 26.5 | 5.63 | 34 | 34 | 3.69 | 9.13 | 9.5 | 10.63 | 12.5 | 13.75 | 16.75 | 3.69 | [10 empty] | 42 | 42 | 2.63 | 4.63 | 5.13 | 5.5 | 5.5 | 5.5 | 5.5 | 2.63 | 42 | 42 | 5.63 | 10.88 | 11.38 | 11.75 | 15.25 | 21 | 26.5 | 5.63
[11 empty] | 36 | 36 | 3.75 | 9.5 | 9.88 | 11.13 | 13.25 | 14.5 | 17.5 | 3.75
[11 empty] | 42 | 42 | 4 | 10.88 | 11.38 | 12.75 | 14 | 15.25 | 18.25 | 4
|  | Weld Neck (FEET) | [9 empty] | Slip-On, Threaded, and Socket (FEET) | [9 empty] | Lap Joint (FEET) | [9 empty] | Blind (FEET) | [9 empty] | Unknown (FEET)
|  | Outside Diameter | Weld Neck_150 LB | Weld Neck_300 LB | Weld Neck_400 LB | Weld Neck_600 LB | Weld Neck_900 LB | Weld Neck_1500 LB | Weld Neck_2500 LB | Weld Neck_Unknown Rating |  | Outside Diameter | Slip-On, Threaded, and Socket_150 LB | Slip-On, Threaded, and Socket_300 LB | Slip-On, Threaded, and Socket_400 LB | Slip-On, Threaded, and Socket_600 LB | Slip-On, Threaded, and Socket_900 LB | Slip-On, Threaded, and Socket_1500 LB | Slip-On, Threaded, and Socket_2500 LB | Slip-On, Threaded, and Socket_Unknown Rating |  | Outside Diameter | Lap Joint_150 LB | Lap Joint_300 LB | Lap Joint_400 LB | Lap Joint_600 LB | Lap Joint_900 LB | Lap Joint_1500 LB | Lap Joint_2500 LB | Lap Joint_Unknown Rating |  | Outside Diameter | Blind_150 LB | Blind_300 LB | Blind_400 LB | Blind_600 LB | Blind_900 LB | Blind_1500 LB | Blind_2500 LB | Blind_Unknown Rating |  | Outside Diameter | Unknown Flange Type_150 LB | Unknown Flange Type_300 LB | Unknown Flange Type_400 LB | Unknown Flange Type_600 LB | Unknown Flange Type_900 LB | Unknown Flange Type_1500 LB | Unknown Flange Type_2500 LB | Unknown Flange Type_Unknown Rating
| 0.5 | 0.84 | 0.15667 | 0.17167 | 0.17167 | 0.17167 | 0.19833 | 0.19833 | 0.24 | 0.15667 | 0.125 | 0.405 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.5 | 0.84 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.5 | 0.84 | 0.036667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.046667 | 0.036667 | 0.5 | 0.84 | 0.15667 | 0.17167 | 0.17167 | 0.17167 | 0.19833 | 0.19833 | 0.24 | 0.15667
| 0.75 | 1.05 | 0.17167 | 0.1875 | 0.1875 | 0.1875 | 0.22917 | 0.22917 | 0.26083 | 0.17167 | 0.25 | 0.54 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 0.75 | 1.05 | 0.0525 | 0.083333 | 0.083333 | 0.083333 | 0.115 | 0.115 | 0.14083 | 0.0525 | 0.75 | 1.05 | 0.041667 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.0525 | 0.041667 | 0.75 | 1.05 | 0.17167 | 0.1875 | 0.1875 | 0.1875 | 0.22917 | 0.22917 | 0.26083 | 0.17167
| 1 | 1.315 | 0.1825 | 0.20333 | 0.20333 | 0.20333 | 0.24 | 0.24 | 0.29167 | 0.1825 | 0.5 | 0.84 | 0.0525 | 0.073333 | 0.073333 | 0.073333 | 0.10417 | 0.10417 | 0.13 | 0.0525 | 1 | 1.315 | 0.0575 | 0.088333 | 0.088333 | 0.088333 | 0.13583 | 0.13583 | 0.15667 | 0.0575 | 1 | 1.315 | 0.046667 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.0575 | 0.046667 | 1 | 1.315 | 0.1825 | 0.20333 | 0.20333 | 0.20333 | 0.24 | 0.24 | 0.29167 | 0.1825
| 1.25 | 1.66 | 0.1875 | 0.21333 | 0.21917 | 0.21917 | 0.24 | 0.24 | 0.3125 | 0.1875 | 0.75 | 1.05 | 0.0525 | 0.083333 | 0.083333 | 0.083333 | 0.115 | 0.115 | 0.14083 | 0.0525 | 1.25 | 1.66 | 0.0675 | 0.088333 | 0.094167 | 0.094167 | 0.13583 | 0.13583 | 0.17167 | 0.0675 | 1.25 | 1.66 | 0.0525 | 0.0625 | 0.0675 | 0.0675 | 0.0675 | 0.0675 | 0.0675 | 0.0525 | 1.25 | 1.66 | 0.1875 | 0.21333 | 0.21917 | 0.21917 | 0.24 | 0.24 | 0.3125 | 0.1875
| 1.5 | 1.9 | 0.20333 | 0.22417 | 0.22917 | 0.22917 | 0.27083 | 0.27083 | 0.365 | 0.20333 | 1 | 1.315 | 0.0575 | 0.088333 | 0.088333 | 0.088333 | 0.13583 | 0.13583 | 0.15667 | 0.0575 | 1.5 | 1.9 | 0.073333 | 0.099167 | 0.10417 | 0.10417 | 0.14583 | 0.14583 | 0.19833 | 0.073333 | 1.5 | 1.9 | 0.0575 | 0.0675 | 0.073333 | 0.073333 | 0.073333 | 0.073333 | 0.073333 | 0.0575 | 1.5 | 1.9 | 0.20333 | 0.22417 | 0.22917 | 0.22917 | 0.27083 | 0.27083 | 0.365 | 0.20333
| 2 | 2.375 | 0.20833 | 0.22917 | 0.24 | 0.24 | 0.33333 | 0.33333 | 0.41667 | 0.20833 | 1.25 | 1.66 | 0.0675 | 0.088333 | 0.094167 | 0.094167 | 0.13583 | 0.13583 | 0.17167 | 0.0675 | 2 | 2.375 | 0.083333 | 0.10917 | 0.12 | 0.12 | 0.1875 | 0.1875 | 0.22917 | 0.083333 | 2 | 2.375 | 0.0625 | 0.073333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.0625 | 2 | 2.375 | 0.20833 | 0.22917 | 0.24 | 0.24 | 0.33333 | 0.33333 | 0.41667 | 0.20833
| 2.5 | 2.875 | 0.22917 | 0.25 | 0.26083 | 0.26083 | 0.34417 | 0.34417 | 0.46917 | 0.22917 | 1.5 | 1.9 | 0.073333 | 0.099167 | 0.10417 | 0.10417 | 0.14583 | 0.14583 | 0.19833 | 0.073333 | 2.5 | 2.875 | 0.094167 | 0.125 | 0.13583 | 0.13583 | 0.20833 | 0.20833 | 0.26083 | 0.094167 | 2.5 | 2.875 | 0.073333 | 0.083333 | 0.094167 | 0.094167 | 0.094167 | 0.094167 | 0.094167 | 0.073333 | 2.5 | 2.875 | 0.22917 | 0.25 | 0.26083 | 0.26083 | 0.34417 | 0.34417 | 0.46917 | 0.22917
| 3 | 3.5 | 0.22917 | 0.26083 | 0.27083 | 0.27083 | 0.33333 | 0.38583 | 0.5525 | 0.22917 | 2 | 2.375 | 0.083333 | 0.10917 | 0.12 | 0.12 | 0.1875 | 0.1875 | 0.22917 | 0.083333 | 3 | 3.5 | 0.099167 | 0.14083 | 0.15083 | 0.15083 | 0.1775 | 0.24 | 0.3025 | 0.099167 | 3 | 3.5 | 0.078333 | 0.094167 | 0.10417 | 0.10417 | 0.10417 | 0.10417 | 0.10417 | 0.078333 | 3 | 3.5 | 0.22917 | 0.26083 | 0.27083 | 0.27083 | 0.33333 | 0.38583 | 0.5525 | 0.22917
| 3.5 | 4 | 0.23417 | 0.26583 | 0.28167 | 0.28167 | 0.33333 | 0.38583 | 0.58917 | 0.23417 | 2.5 | 2.875 | 0.094167 | 0.125 | 0.13583 | 0.13583 | 0.20833 | 0.20833 | 0.26083 | 0.094167 | 3.5 | 4 | 0.10417 | 0.14583 | 0.16167 | 0.16167 | 0.1775 | 0.24 | 0.32833 | 0.10417 | 3.5 | 4 | 0.078333 | 0.099167 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.078333 | 3.5 | 4 | 0.23417 | 0.26583 | 0.28167 | 0.28167 | 0.33333 | 0.38583 | 0.58917 | 0.23417
| 4 | 4.5 | 0.25 | 0.28167 | 0.29167 | 0.33333 | 0.375 | 0.40667 | 0.625 | 0.25 | 3 | 3.5 | 0.099167 | 0.14083 | 0.15083 | 0.15083 | 0.1775 | 0.24 | 0.3025 | 0.099167 | 4 | 4.5 | 0.10917 | 0.15667 | 0.16667 | 0.1775 | 0.22917 | 0.29667 | 0.35417 | 0.10917 | 4 | 4.5 | 0.078333 | 0.10417 | 0.115 | 0.125 | 0.125 | 0.125 | 0.125 | 0.078333 | 4 | 4.5 | 0.25 | 0.28167 | 0.29167 | 0.33333 | 0.375 | 0.40667 | 0.625 | 0.25
| 5 | 5.563 | 0.29167 | 0.32333 | 0.33333 | 0.375 | 0.41667 | 0.51083 | 0.75 | 0.29167 | 3.5 | 4 | 0.10417 | 0.14583 | 0.16167 | 0.16167 | 0.1775 | 0.24 | 0.32833 | 0.10417 | 5 | 5.563 | 0.12 | 0.16667 | 0.1775 | 0.19833 | 0.26083 | 0.34417 | 0.4275 | 0.12 | 5 | 5.563 | 0.078333 | 0.115 | 0.125 | 0.14583 | 0.14583 | 0.14583 | 0.14583 | 0.078333 | 5 | 5.563 | 0.29167 | 0.32333 | 0.33333 | 0.375 | 0.41667 | 0.51083 | 0.75 | 0.29167
| 6 | 6.625 | 0.29167 | 0.32333 | 0.33833 | 0.38583 | 0.45833 | 0.5625 | 0.89583 | 0.29167 | 4 | 4.5 | 0.10917 | 0.15667 | 0.16667 | 0.1775 | 0.22917 | 0.29667 | 0.35417 | 0.10917 | 6 | 6.625 | 0.13 | 0.17167 | 0.1875 | 0.21917 | 0.28167 | 0.39083 | 0.5 | 0.13 | 6 | 6.625 | 0.083333 | 0.12 | 0.13583 | 0.15667 | 0.15667 | 0.15667 | 0.15667 | 0.083333 | 6 | 6.625 | 0.29167 | 0.32333 | 0.33833 | 0.38583 | 0.45833 | 0.5625 | 0.89583 | 0.29167
| 8 | 8.625 | 0.33333 | 0.365 | 0.38583 | 0.4375 | 0.53167 | 0.69833 | 1.0417 | 0.33333 | 5 | 5.563 | 0.12 | 0.16667 | 0.1775 | 0.19833 | 0.26083 | 0.34417 | 0.4275 | 0.12 | 8 | 8.625 | 0.14583 | 0.20333 | 0.22417 | 0.25 | 0.375 | 0.46917 | 0.58333 | 0.14583 | 8 | 8.625 | 0.094167 | 0.13583 | 0.15667 | 0.1825 | 0.1825 | 0.1825 | 0.1825 | 0.094167 | 8 | 8.625 | 0.33333 | 0.365 | 0.38583 | 0.4375 | 0.53167 | 0.69833 | 1.0417 | 0.33333
| 10 | 10.75 | 0.33333 | 0.38583 | 0.40667 | 0.5 | 0.60417 | 0.83333 | 1.375 | 0.33333 | 6 | 6.625 | 0.13 | 0.17167 | 0.1875 | 0.21917 | 0.28167 | 0.39083 | 0.5 | 0.13 | 10 | 10.75 | 0.16167 | 0.3125 | 0.33333 | 0.365 | 0.41667 | 0.58333 | 0.75 | 0.16167 | 10 | 10.75 | 0.099167 | 0.15667 | 0.1775 | 0.20833 | 0.20833 | 0.20833 | 0.20833 | 0.099167 | 10 | 10.75 | 0.33333 | 0.38583 | 0.40667 | 0.5 | 0.60417 | 0.83333 | 1.375 | 0.33333
| 12 | 12.75 | 0.375 | 0.4275 | 0.44833 | 0.51083 | 0.65667 | 0.9275 | 1.5208 | 0.375 | 8 | 8.625 | 0.14583 | 0.20333 | 0.22417 | 0.25 | 0.33333 | 0.46917 | 0.58333 | 0.14583 | 12 | 12.75 | 0.1825 | 0.33333 | 0.35417 | 0.38583 | 0.46917 | 0.71917 | 0.83333 | 0.1825 | 12 | 12.75 | 0.10417 | 0.16667 | 0.1875 | 0.21917 | 0.21917 | 0.21917 | 0.21917 | 0.10417 | 12 | 12.75 | 0.375 | 0.4275 | 0.44833 | 0.51083 | 0.65667 | 0.9275 | 1.5208 | 0.375
| 14 | 14 | 0.41667 | 0.46917 | 0.49 | 0.54167 | 0.69833 | 0.97917 | 1.5833 | 0.41667 | 10 | 10.75 | 0.16167 | 0.21917 | 0.24 | 0.28167 | 0.35417 | 0.52083 | 0.75 | 0.16167 | 14 | 14 | 0.26083 | 0.365 | 0.38583 | 0.41667 | 0.51083 | 0.79167 | 0.89583 | 0.26083 | 14 | 14 | 0.115 | 0.1775 | 0.19833 | 0.22917 | 0.22917 | 0.22917 | 0.22917 | 0.115 | 14 | 14 | 0.41667 | 0.46917 | 0.49 | 0.54167 | 0.69833 | 0.97917 | 1.5833 | 0.41667
| 16 | 16 | 0.41667 | 0.47917 | 0.5 | 0.58333 | 0.70833 | 1.0208 | 1.6458 | 0.41667 | 12 | 12.75 | 0.1825 | 0.24 | 0.26083 | 0.3025 | 0.38583 | 0.59417 | 0.83333 | 0.1825 | 16 | 16 | 0.28667 | 0.39583 | 0.41667 | 0.45833 | 0.54167 | 0.85417 | 0.95833 | 0.28667 | 16 | 16 | 0.12 | 0.1875 | 0.20833 | 0.25 | 0.25 | 0.25 | 0.25 | 0.12 | 16 | 16 | 0.41667 | 0.47917 | 0.5 | 0.58333 | 0.70833 | 1.0208 | 1.6458 | 0.41667
| 18 | 18 | 0.45833 | 0.52083 | 0.54167 | 0.60417 | 0.75 | 1.0733 | 1.7083 | 0.45833 | 14 | 14 | 0.1875 | 0.25 | 0.27583 | 0.3075 | 0.4275 | 0.64583 | 0.89583 | 0.1875 | 18 | 18 | 0.26583 | 0.4275 | 0.44833 | 0.5 | 0.625 | 0.90667 | 1.0208 | 0.26583 | 18 | 18 | 0.13 | 0.19833 | 0.21917 | 0.27083 | 0.27083 | 0.27083 | 0.27083 | 0.13 | 18 | 18 | 0.45833 | 0.52083 | 0.54167 | 0.60417 | 0.75 | 1.0733 | 1.7083 | 0.45833
| 20 | 20 | 0.47417 | 0.53167 | 0.5525 | 0.625 | 0.8125 | 1.1667 | 1.7708 | 0.47417 | 16 | 16 | 0.20833 | 0.27083 | 0.3075 | 0.34917 | 0.4375 | 0.70833 | 0.95833 | 0.20833 | 20 | 20 | 0.33833 | 0.45833 | 0.47917 | 0.54167 | 0.6875 | 0.95833 | 1.0833 | 0.33833 | 20 | 20 | 0.14083 | 0.20833 | 0.22917 | 0.29167 | 0.29167 | 0.29167 | 0.29167 | 0.14083 | 20 | 20 | 0.47417 | 0.53167 | 0.5525 | 0.625 | 0.8125 | 1.1667 | 1.7708 | 0.47417
| 22 | 22 | 0.49 | 0.54167 | 0.5625 | 0.64583 | 0.88583 | 1.25 | 1.8333 | 0.49 | 18 | 18 | 0.22417 | 0.29167 | 0.32333 | 0.38583 | 0.5 | 0.77083 | 1.0208 | 0.22417 | 24 | 24 | 0.365 | 0.5 | 0.52083 | 0.60417 | 0.875 | 1.0833 | 1.1458 | 0.365 | 22 | 22 | 0.15083 | 0.21917 | 0.24 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.15083 | 22 | 22 | 0.49 | 0.54167 | 0.5625 | 0.64583 | 0.88583 | 1.25 | 1.8333 | 0.49
| 24 | 24 | 0.5 | 0.5525 | 0.57333 | 0.66667 | 0.95833 | 1.3333 | 1.8958 | 0.5 | 20 | 20 | 0.24 | 0.3125 | 0.33333 | 0.41667 | 0.52083 | 0.83333 | 1.0833 | 0.24 | [10 empty] | 24 | 24 | 0.15667 | 0.22917 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.15667 | 24 | 24 | 0.5 | 0.5525 | 0.57333 | 0.66667 | 0.95833 | 1.3333 | 1.8958 | 0.5
| 26 | 26 | 0.41667 | 0.60417 | 0.63583 | 0.72917 | 1.0208 | 1.4167 | 1.9583 | 0.41667 | 22 | 22 | 0.26083 | 0.33333 | 0.35417 | 0.4375 | 0.59417 | 0.89583 | 1.1458 | 0.26083 | [10 empty] | 26 | 26 | 0.16667 | 0.26083 | 0.29167 | 0.35417 | 0.35417 | 0.35417 | 0.35417 | 0.16667 | 26 | 26 | 0.41667 | 0.60417 | 0.63583 | 0.72917 | 1.0208 | 1.4167 | 1.9583 | 0.41667
| 30 | 30 | 0.4275 | 0.6875 | 0.71917 | 0.79167 | 1.0833 | 1.5 | 2.0208 | 0.4275 | 24 | 24 | 0.27083 | 0.34917 | 0.375 | 0.45833 | 0.66667 | 0.95833 | 1.2083 | 0.27083 | [10 empty] | 30 | 30 | 0.1775 | 0.3025 | 0.33333 | 0.375 | 0.375 | 0.375 | 0.375 | 0.1775 | 30 | 30 | 0.4275 | 0.6875 | 0.71917 | 0.79167 | 1.0833 | 1.5 | 2.0208 | 0.4275
| 34 | 34 | 0.4425 | 0.76083 | 0.79167 | 0.85417 | 1.1458 | 1.5833 | 2.0833 | 0.4425 | 26 | 26 | 0.28167 | 0.60417 | 0.63583 | 0.72917 | 0.91667 | 1.0208 | 1.2708 | 0.28167 | [10 empty] | 34 | 34 | 0.1925 | 0.33333 | 0.365 | 0.39583 | 0.39583 | 0.39583 | 0.39583 | 0.1925 | 34 | 34 | 0.4425 | 0.76083 | 0.79167 | 0.85417 | 1.1458 | 1.5833 | 2.0833 | 0.4425
| 36 | 36 | 0.44833 | 0.79167 | 0.82333 | 0.91667 | 1.2083 | 1.6667 | 2.1458 | 0.44833 | 30 | 30 | 0.29167 | 0.6875 | 0.71917 | 0.8125 | 0.97917 | 1.0833 | 1.3333 | 0.29167 | [10 empty] | 36 | 36 | 0.19833 | 0.34417 | 0.375 | 0.40667 | 0.40667 | 0.40667 | 0.40667 | 0.19833 | 36 | 36 | 0.44833 | 0.79167 | 0.82333 | 0.91667 | 1.2083 | 1.6667 | 2.1458 | 0.44833
| 42 | 42 | 0.46917 | 0.90667 | 0.94833 | 0.97917 | 1.2708 | 1.75 | 2.2083 | 0.46917 | 34 | 34 | 0.3075 | 0.76083 | 0.79167 | 0.88583 | 1.0417 | 1.1458 | 1.3958 | 0.3075 | [10 empty] | 42 | 42 | 0.21917 | 0.38583 | 0.4275 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.21917 | 42 | 42 | 0.46917 | 0.90667 | 0.94833 | 0.97917 | 1.2708 | 1.75 | 2.2083 | 0.46917
[11 empty] | 36 | 36 | 0.3125 | 0.79167 | 0.82333 | 0.9275 | 1.1042 | 1.2083 | 1.4583 | 0.3125
[11 empty] | 42 | 42 | 0.33333 | 0.90667 | 0.94833 | 1.0625 | 1.1667 | 1.2708 | 1.5208 | 0.33333
| Feature | Length Lookup
| Flange | Weld Neck_150 LB
Weld Neck_300 LB
Weld Neck_400 LB
Weld Neck_600 LB
Weld Neck_900 LB
Weld Neck_1500 LB
Weld Neck_2500 LB
Weld Neck_Unknown Rating
Slip-On, Threaded, and Socket_150 LB
Slip-On, Threaded, and Socket_300 LB
Slip-On, Threaded, and Socket_400 LB
Slip-On, Threaded, and Socket_600 LB
Slip-On, Threaded, and Socket_900 LB
Slip-On, Threaded, and Socket_1500 LB
Slip-On, Threaded, and Socket_2500 LB
Slip-On, Threaded, and Socket_Unknown Rating
Lap Joint_150 LB
Lap Joint_300 LB
Lap Joint_400 LB
Lap Joint_600 LB
Lap Joint_900 LB
Lap Joint_1500 LB
Lap Joint_2500 LB
Lap Joint_Unknown Rating
Blind_150 LB
Blind_300 LB
Blind_400 LB
Blind_600 LB
Blind_900 LB
Blind_1500 LB
Blind_2500 LB
Blind_Unknown Rating
Unknown Flange Type_150 LB
Unknown Flange Type_300 LB
Unknown Flange Type_400 LB
Unknown Flange Type_600 LB
Unknown Flange Type_900 LB
Unknown Flange Type_1500 LB
Unknown Flange Type_2500 LB
Unknown Flange Type_Unknown Rating

## Tee Length (hidden)
If OD is missing, do not calculate length
| Tee | Run OD | Branch OD | Orientation
|  | 8 | 3 | Straight | 14"
|  | 8 | 3 | Branch | 6"
|  |  | Feet | Feet | Feet
|  | Outside Diameter | Run Length_Straight or Reducing | Branch Length_Straight Tee | Branch Length_Reducing Tee
| 0.5 | 0.84 | 0.16667 | 0.083333 | 0.083333
| 0.75 | 1.05 | 0.18833 | 0.094167 | 0.094167
| 1 | 1.315 | 0.25 | 0.125 | 0.125
| 1.25 | 1.66 | 0.31333 | 0.15667 | 0.15667
| 1.5 | 1.9 | 0.375 | 0.1875 | 0.1875
| 2 | 2.375 | 0.41667 | 0.20833 | 0.175
| 2.5 | 2.875 | 0.5 | 0.25 | 0.21104
| 3 | 3.5 | 0.56333 | 0.28167 | 0.2475
| 3.5 | 4 | 0.625 | 0.3125 | 0.28146
| 4 | 4.5 | 0.68833 | 0.34417 | 0.3085
| 5 | 5.563 | 0.81333 | 0.40667 | 0.36483
| 6 | 6.625 | 0.93833 | 0.46917 | 0.419
| 8 | 8.625 | 1.1667 | 0.58333 | 0.52375
| 10 | 10.75 | 1.4167 | 0.70833 | 0.63292
| 12 | 12.75 | 1.6667 | 0.83333 | 0.74229
| 14 | 14 | 1.8333 | 0.91667 | 0.83104
| 16 | 16 | 2 | 1 | 0.9315
| 18 | 18 | 2.25 | 1.125 | 1.0418
| 20 | 20 | 2.5 | 1.25 | 1.139
| 22 | 22 | 2.75 | 1.375 | 1.2536
| 24 | 24 | 2.8333 | 1.4167 | 1.3508
| 26 | 26 | 3.25 | 1.625 | 1.4718
| 30 | 30 | 3.6667 | 1.8333 | 1.6417
| 34 | 34 | 4.1667 | 2.0833 | 1.9028
| 36 | 36 | 4.4167 | 2.2083 | 1.9417
| 42 | 42 | 5 | 2.5 | 2.2667
| Feature | Length Lookup
| Tee | Run Length_Straight or Reducing Tee
Branch Length_Straight Tee
Branch Length_Reducing Tee
|  |  | INCH | INCH | INCH
Inches |  | Outside Diameter | Run Length_Straight or Reducing | Branch Length_Straight Tee | Branch Length_Reducing Tee
| 0.5 | 0.84 | 1 | 1 | 1
| 0.75 | 1.05 | 1.13 | 1.13 | 1.13
| 1 | 1.315 | 1.5 | 1.5 | 1.5
| 1.25 | 1.66 | 1.88 | 1.88 | 1.88
| 1.5 | 1.9 | 2.25 | 2.25 | 2.25
| 2 | 2.375 | 2.5 | 2.5 | 2.1
| 2.5 | 2.875 | 3 | 3 | 2.5325
| 3 | 3.5 | 3.38 | 3.38 | 2.97
| 3.5 | 4 | 3.75 | 3.75 | 3.3775
| 4 | 4.5 | 4.13 | 4.13 | 3.702
| 5 | 5.563 | 4.88 | 4.88 | 4.378
| 6 | 6.625 | 5.63 | 5.63 | 5.028
| 8 | 8.625 | 7 | 7 | 6.285
| 10 | 10.75 | 8.5 | 8.5 | 7.595
| 12 | 12.75 | 10 | 10 | 8.9075
| 14 | 14 | 11 | 11 | 9.9725
| 16 | 16 | 12 | 12 | 11.178
| 18 | 18 | 13.5 | 13.5 | 12.502
| 20 | 20 | 15 | 15 | 13.6683
| 22 | 22 | 16.5 | 16.5 | 15.0433
| 24 | 24 | 17 | 17 | 16.21
| 26 | 26 | 19.5 | 19.5 | 17.6614
| 30 | 30 | 22 | 22 | 19.7
| 34 | 34 | 25 | 25 | 22.8333
| 36 | 36 | 26.5 | 26.5 | 23.3
| 42 | 42 | 30 | 30 | 27.2

## Reducer Length (hidden)
If OD is missing, do not calculate length
No reducer type drop down, Only need OD
Feet
|  | Outside Diameter | Length_Concentric and Eccentric
| 0.75 | 1.05 | 0.125
| 1 | 1.315 | 0.16667
| 1.25 | 1.66 | 0.16667
| 1.5 | 1.9 | 0.20833
| 2 | 2.375 | 0.25
| 2.5 | 2.875 | 0.29167
| 3 | 3.5 | 0.29167
| 3.5 | 4 | 0.33333
| 4 | 4.5 | 0.33333
| 5 | 5.563 | 0.41667
| 6 | 6.625 | 0.45833
| 8 | 8.625 | 0.5
| 10 | 10.75 | 0.58333
| 12 | 12.75 | 0.66667
| 14 | 14 | 1.0833
| 16 | 16 | 1.1667
| 18 | 18 | 1.25
| 20 | 20 | 1.6667
| 22 | 22 | 1.6667
| 24 | 24 | 1.6667
| 26 | 26 | 2
| 30 | 30 | 2
| 34 | 34 | 2
| 36 | 36 | 2
| 42 | 42 | 2
INCH
|  | Outside Diameter | Run Length_Straight or Reducing
| 0.75 | 1.05 | 1.5
| 1 | 1.315 | 2
| 1.25 | 1.66 | 2
| 1.5 | 1.9 | 2.5
| 2 | 2.375 | 3
| 2.5 | 2.875 | 3.5
| 3 | 3.5 | 3.5
| 3.5 | 4 | 4
| 4 | 4.5 | 4
| 5 | 5.563 | 5
| 6 | 6.625 | 5.5
| 8 | 8.625 | 6
| 10 | 10.75 | 7
| 12 | 12.75 | 8
| 14 | 14 | 13
| 16 | 16 | 14
| 18 | 18 | 15
| 20 | 20 | 20
| 22 | 22 | 20
| 24 | 24 | 20
| 26 | 26 | 24
| 30 | 30 | 24
| 34 | 34 | 24
| 36 | 36 | 24
| 42 | 42 | 24

## Cap Length (hidden)
If OD is missing, do not calculate length
No Cap type drop down, Only need OD
Feet
|  | Outside Diameter | Length_Cap
| 0.5 | 0.84 | 0.083333
| 0.75 | 1.05 | 0.083333
| 1 | 1.315 | 0.125
| 1.25 | 1.66 | 0.125
| 1.5 | 1.9 | 0.125
| 2 | 2.375 | 0.125
| 2.5 | 2.875 | 0.125
| 3 | 3.5 | 0.16667
| 3.5 | 4 | 0.20833
| 4 | 4.5 | 0.20833
| 5 | 5.563 | 0.25
| 6 | 6.625 | 0.29167
| 8 | 8.625 | 0.33333
| 10 | 10.75 | 0.41667
| 12 | 12.75 | 0.5
| 14 | 14 | 0.54167
| 16 | 16 | 0.58333
| 18 | 18 | 0.66667
| 20 | 20 | 0.75
| 22 | 22 | 0.83333
| 24 | 24 | 0.875
| 26 | 26 | 0.875
| 30 | 30 | 0.875
| 34 | 34 | 0.875
| 36 | 36 | 0.875
| 42 | 42 | 1
INCH
|  | Outside Diameter | Length_Cap
| 0.5 | 0.84 | 1
| 0.75 | 1.05 | 1
| 1 | 1.315 | 1.5
| 1.25 | 1.66 | 1.5
| 1.5 | 1.9 | 1.5
| 2 | 2.375 | 1.5
| 2.5 | 2.875 | 1.5
| 3 | 3.5 | 2
| 3.5 | 4 | 2.5
| 4 | 4.5 | 2.5
| 5 | 5.563 | 3
| 6 | 6.625 | 3.5
| 8 | 8.625 | 4
| 10 | 10.75 | 5
| 12 | 12.75 | 6
| 14 | 14 | 6.5
| 16 | 16 | 7
| 18 | 18 | 8
| 20 | 20 | 9
| 22 | 22 | 10
| 24 | 24 | 10.5
| 26 | 26 | 10.5
| 30 | 30 | 10.5
| 34 | 34 | 10.5
| 36 | 36 | 10.5
| 42 | 42 | 12

## Cross Length (hidden)
If OD is missing, do not calculate length
No Cross type drop down, Only need OD
Feet
|  | Outside Diameter | Length_Cap
| 1.25 | 1.66 | 0.15667
| 1.5 | 1.9 | 0.1875
| 2 | 2.375 | 0.20833
| 2.5 | 2.875 | 0.25
| 3 | 3.5 | 0.28167
| 3.5 | 4 | 0.3125
| 4 | 4.5 | 0.34417
| 5 | 5.563 | 0.40667
| 6 | 6.625 | 0.46917
| 8 | 8.625 | 0.58333
| 10 | 10.75 | 0.70833
| 12 | 12.75 | 0.83333
| 14 | 14 | 0.91667
| 16 | 16 | 1
| 18 | 18 | 1.125
| 20 | 20 | 1.25
| 22 | 22 | 1.375
| 24 | 24 | 1.4167
| 26 | 26 | 1.625
| 30 | 30 | 1.8333
| 34 | 34 | 2.0833
INCH
|  | Outside Diameter | Length_Cap
| 1.25 | 1.66 | 1.88
| 1.5 | 1.9 | 2.25
| 2 | 2.375 | 2.5
| 2.5 | 2.875 | 3
| 3 | 3.5 | 3.38
| 3.5 | 4 | 3.75
| 4 | 4.5 | 4.13
| 5 | 5.563 | 4.88
| 6 | 6.625 | 5.63
| 8 | 8.625 | 7
| 10 | 10.75 | 8.5
| 12 | 12.75 | 10
| 14 | 14 | 11
| 16 | 16 | 12
| 18 | 18 | 13.5
| 20 | 20 | 15
| 22 | 22 | 16.5
| 24 | 24 | 17
| 26 | 26 | 19.5
| 30 | 30 | 22
| 34 | 34 | 25

## Valve Length (hidden)
If OD is missing, do not calculate length |  | Flange | Nominal Outside Diameter | Valve Type |  | Rating Class
|  |  |  | Plug |  | 150
If Rating = unknown: default to 150 LB |  |  |  | Ball |  | 300
|  |  |  | Gate |  | 400
600
900
|  |  |  | Unknown |  | 1500
2500
Unknown
|  | Weld by Weld_Plug Valve (INCHES) | [8 empty] | Flange by Flange_Plug Valve (INCHES) | [8 empty] | Weld by Weld_Ball Valve (INCHES) | [8 empty] | Flange by Flange_Ball Valve (INCHES) | [8 empty] | Final (INCHES)
|  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | Rating Class 150 LB (285 psi) | Rating Class 300 LB (740 psi) | Rating Class 400 LB (990 psi) | Rating Class 600 LB (1480 psi) | Rating Class 900 LB (2220 psi) | Rating Class 1500 LB (3705 psi) | Rating Class 2500 LB (6170 psi) | Less than Rating Class 150 LB (285 psi) | Greater than Rating Class 2500 LB (6170 psi) | Unknown Rating Class
| 0.5 | 0.84 | 4.25 | 4.25 | [5 empty] | 0.5 | 0.84 |  |  |  | 4.25 |  |  |  | 0.5 | 0.84 | [7 empty] | 0.5 | 0.84 | [7 empty] | 0.5 | 0.84 | 4.25 | 5.25 | 6.25 | 6.75 | 8.5 | 10.75 | 11 | 4.25 | 11 | 4.25
| 0.75 | 1.05 | 4.25 | 4.25 | [5 empty] | 0.75 | 1.05 |  |  |  | 4.25 |  |  |  | 0.75 | 1.05 | [7 empty] | 0.75 | 1.05 | [7 empty] | 0.75 | 1.05 | 4.25 | 5.75 | 6.75 | 7.25 | 9.25 | 11.5 | 12 | 4.25 | 12 | 4.25
| 1 | 1.315 | 5.5 | 4.5 |  | 8.5 |  | 10 |  | 1 | 1.315 | 5.5 | 6.25 |  | 8.5 |  | 10 |  | 1 | 1.315 | [7 empty] | 1 | 1.315 | [7 empty] | 1 | 1.315 | 5.5 | 6.25 | 7 | 8.5 | 10 | 12.25 | 13 | 5.5 | 13 | 5.5
| 1.5 | 1.9 | 6.5 | 5.5 | [5 empty] | 1.5 | 1.9 | 6.5 | 7.5 |  | 5.75 |  |  |  | 1.25 | 1.66 | [7 empty] | 1.25 | 1.66 | [7 empty] | 1.25 | 1.66 | 5.5 | 6.88 | 7.75 | 9.25 | 10.75 | 13 | 14.19 | 5.5 | 14.19 | 5.5
| 2 | 2.375 | 10.5 | 10.5 |  | 11.5 |  | 14.5 | 17.75 | 2 | 2.375 | 7 | 8.5 |  | 11.5 |  | 14.5 | 17.88 | 1.5 | 1.9 | [7 empty] | 1.5 | 1.9 | [7 empty] | 1.5 | 1.9 | 6.5 | 7.5 | 8.5 | 10 | 11.5 | 13.75 | 15.38 | 6.5 | 15.38 | 6.5
| 2.5 | 2.875 | 7.5 | 9.5 | [5 empty] | 2.5 | 2.875 | 7.5 | 9.5 |  | 9.5 |  |  |  | 2 | 2.375 | 11 | 11 |  | 11 | 11 | 11 | 15 | 2 | 2.375 | 7 | 8.5 | 11.5 | 11.5 | 14.5 | 14.5 | 17.75 | 2 | 2.375 | 7 | 8.5 | 9.5 | 11.5 | 13.5 | 14.5 | 17.75 | 7 | 17.75 | 7
| 3 | 3.5 | 13 | 13 |  | 14 | 18.5 | 18.5 |  | 3 | 3.5 | 8 | 11.13 |  | 14 | 15 | 18.5 | 23 | 2.5 | 2.875 | [7 empty] | 2.5 | 2.875 | [7 empty] | 2.5 | 2.875 | 7.5 | 9.5 | 12 | 12.75 | 14.75 | 16.5 | 21.13 | 7.5 | 21.13 | 7.5
| 4 | 4.5 | 14 | 14 | 16 | 17 | 21.5 | 21.5 | 26.5 | 4 | 4.5 | 9 | 12 | 16 | 17 | 18 | 21.5 | 26.88 | 3 | 3.5 | 12.5 | 12.5 |  | 12.5 | 13.5 | 13.5 | 18 | 3 | 3.5 | 8 | 11.125 | 14 | 14 | 15 | 18.5 | 22.75 | 3 | 3.5 | 8 | 11.125 | 13.5 | 14 | 15 | 18.5 | 22.75 | 8 | 22.75 | 8
| 6 | 6.625 | 18 | 18 | 19.5 | 18 | 18 | 27.6 | 36 | 6 | 6.625 | 10.5 | 15.88 | 19.5 | 22 | 24 | 27.75 | 36.5 | 3.5 | 4 | [7 empty] | 3.5 | 4 | [7 empty] | 3.5 | 4 | 8.5 | 11.57 | 15 | 15.5 | 16.5 | 20 | 24.63 | 8.5 | 24.63 | 8.5
| 8 | 8.625 | 20.5 | 20.25 | 23.5 | 20.5 | 20.5 | 32.75 | 40.25 | 8 | 8.625 | 11.5 | 16.5 | 23.5 | 26 | 29 | 32.75 | 40.88 | 4 | 4.5 | 14 | 14 | 14 | 14 | 15 | 15 | 20 | 4 | 4.5 | 9 | 12 | 16 | 17 | 18 | 21.5 | 26.5 | 4 | 4.5 | 9 | 12 | 16 | 17 | 18 | 21.5 | 26.5 | 9 | 26.5 | 9
| 10 | 10.75 | 18 | 22 | 26.5 | 24 | 24 | 39 | 50 | 10 | 10.75 | 13 | 18 | 26.5 | 31 | 33 | 39 | 50.88 | 5 | 5.563 | [7 empty] | 5 | 5.563 | [7 empty] | 5 | 5.563 | 12 | 13.94 | 17.75 | 19.5 | 21 | 24.63 | 31.25 | 12 | 31.25 | 12
| 12 | 12.75 | 19.75 | 25 | 30 | 28 | 38 | 44.5 | 56 | 12 | 12.75 | 14 | 19.75 | 30 | 33 | 38 | 44.5 | 56.88 | 6 | 6.625 | 18 | 18 | 18 | 18 | 20 | 20 | 24 | 6 | 6.625 | 15.5 | 15.875 | 19.5 | 22 | 24 | 27.75 | 36 | 6 | 6.625 | 15.5 | 15.875 | 19.5 | 22 | 24 | 27.75 | 36 | 15.5 | 36 | 15.5
| 14 | 14 | 27 | 30 |  | 30 |  |  |  | 14 | 14 | 27 | 30 |  | 35 |  |  |  | 8 | 8.625 | 21.5 | 21.5 | 21.5 | 21.5 | 23.5 | 23.5 | 28 | 8 | 8.625 | 18 | 19.75 | 23.5 | 26 | 29 | 32.75 | 40.5 | 8 | 8.625 | 18 | 19.75 | 23.5 | 26 | 29 | 32.75 | 40.5 | 18 | 40.5 | 18
| 16 | 16 | 30 | 33 |  | 33 | 44.5 | 54.5 | 65 | 16 | 16 | 30 | 33 |  | 39 | 44.5 | 54.5 | 65 | 10 | 10.75 | 23.5 | 23.5 | 23.5 | 23.5 | 25.5 | 25.5 | 33 | 10 | 10.75 | 21 | 22.375 | 26.5 | 31 | 33 | 39 | 50 | 10 | 10.75 | 21 | 22.375 | 26.5 | 31 | 33 | 39 | 50 | 21 | 50 | 21
| 18 | 18 | 34 |  |  | 42 |  |  |  | 18 | 18 | 34 |  |  | 43 |  |  |  | 12 | 12.75 | 26.5 | 26.5 | 26.5 | 26.5 | 29.5 | 29.5 | 36 | 12 | 12.75 | 24 | 25.5 | 30 | 33 | 38 | 44.5 | 56 | 12 | 12.75 | 24 | 25.5 | 30 | 33 | 38 | 44.5 | 56 | 24 | 56 | 24
| 20 | 20 | 36 | 39 |  | 47 | 52 |  |  | 20 | 20 | 36 | 39 |  | 47 | 52 |  |  | 14 | 14 | 28.5 | 28.5 | 28.5 | 28.5 | 31.5 | 31.5 |  | 14 | 14 | 27 | 30 | 32.5 | 35 | 40.5 | 49.5 |  | 14 | 14 | 27 | 30 | 32.5 | 35 | 40.5 | 49.5 | 61 | 27 | 61 | 27
| 24 | 24 | 42 | 45 |  | 55 |  |  |  | 24 | 24 | 42 | 45 |  | 55 |  |  |  | 16 | 16 | 30.5 | 30.5 | 30.5 | 30.5 | 33.5 | 33.5 |  | 16 | 16 | 30 | 33 | 35.5 | 39 | 44.5 | 54.5 |  | 16 | 16 | 30 | 33 | 35.5 | 39 | 44.5 | 54.5 | 66 | 30 | 66 | 30
| 30 | 30 | 51 | [6 empty] | 30 | 30 | 51 | [6 empty] | 18 | 18 | 33.5 | 33.5 | 33.5 | 33.5 | 36.5 | 36.5 |  | 18 | 18 | 34 | 36 | 38.5 | 43 | 48 | 60.5 |  | 18 | 18 | 34 | 36 | 38.5 | 43 | 48 | 60.5 | 71 | 34 | 71 | 34
[19 empty] | 20 | 20 | 35.5 | 35.5 | 35.5 | 35.5 | 38.5 | 38.58 |  | 20 | 20 | 36 | 39 | 41.5 | 47 | 52 | 65.5 |  | 20 | 20 | 36 | 39 | 41.5 | 47 | 52 | 65.5 | 76 | 36 | 76 | 36
[19 empty] | 22 | 22 | 38.5 | 38.5 | 38.5 | 38.5 |  |  |  | 22 | 22 | 40 | 43 | 45 | 51 |  |  |  | 22 | 22 | 40 | 43 | 45 | 51 | 56.5 | 71 | 81 | 40 | 81 | 40
[19 empty] | 24 | 24 | 42 | 42 | 42 | 42 | 45 | 45 |  | 24 | 24 | 42 | 24 | 48.5 | 55 | 61 | 76.5 |  | 24 | 24 | 42 | 45 | 48.5 | 55 | 61 | 76.5 | 86 | 42 | 86 | 42
[19 empty] | 26 | 26 | 44.5 | 44.5 | 44.5 | 44.5 |  |  |  | 26 | 26 | 45 | 49 | 54.5 | 57 |  |  |  | 26 | 26 | 45 | 49 | 54.5 | 57 | 68 | 82.5 | 91 | 45 | 91 | 45
[19 empty] | 30 | 30 | 49 | 49 | 49 | 49 | 52 |  |  | 30 | 30 | 51 | 55 | 60 | 65 | 75 |  |  | 30 | 30 | 51 | 55 | 60 | 65 | 75 | 88.5 | 96 | 51 | 96 | 51
[19 empty] | 34 | 34 | 54.5 | 54.5 | 54.5 | 54.5 |  |  |  | 34 | 34 | 58 | 64 | 70 | 76 |  |  |  | 34 | 34 | 58 | 64 | 70 | 76 | 82.5 | 94.5 | 101 | 58 | 101 | 58
[19 empty] | 36 | 36 | 56.5 | 56.5 | 56.5 | 56.5 | 59.5 |  |  | 36 | 36 | 60 | 68 | 74 | 82 | 90 |  |  | 36 | 36 | 60 | 68 | 74 | 82 | 90 | 100 | 106 | 60 | 106 | 60
[19 empty] | 42 | 42 | 66.5 | 66.5 | 66.5 | 66.5 |  |  |  | 42 | 42 | 72 | 76 | 81 | 83 |  |  |  | 42 | 42 | 72 | 76 | 81 | 83 | 100 | 106 | 111 | 72 | 111 | 72
|  | Weld Neck (FEET) | [8 empty] | Slip-On, Threaded, and Socket (FEET) | [8 empty] | Lap Joint (FEET) | [8 empty] | Blind (FEET) | [8 empty] | Final (FEET)
|  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | 150 LB | 300 LB | 400 LB | 600 LB | 900 LB | 1500 LB | 2500 LB |  | Outside Diameter | Rating Class 150 LB (285 psi) | Rating Class 300 LB (740 psi) | Rating Class 400 LB (990 psi) | Rating Class 600 LB (1480 psi) | Rating Class 900 LB (2220 psi) | Rating Class 1500 LB (3705 psi) | Rating Class 2500 LB (6170 psi) | Less than Rating Class 150 LB (285 psi) | Greater than Rating Class 2500 LB (6170 psi) | Unknown Rating Class
| 0.5 | 0.84 | 4.25 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.84 | 0 | 0 | 0 | 0.35417 | 0 | 0 | 0 | 0.5 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.84 | 0.35417 | 0.4375 | 0.52083 | 0.5625 | 0.70833 | 0.89583 | 0.91667 | 0.35417 | 0.91667 | 0.35417
| 0.75 | 1.05 | 4.25 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05 | 0 | 0 | 0 | 0.35417 | 0 | 0 | 0 | 0.75 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 1.05 | 0.35417 | 0.47917 | 0.5625 | 0.60417 | 0.77083 | 0.95833 | 1 | 0.35417 | 1 | 0.35417
| 1 | 1.315 | 5.5 | 4.5 | 0 | 8.5 | 0 | 10 | 0 | 1 | 1.315 | 0.45833 | 0.52083 | 0 | 0.70833 | 0 | 0.83333 | 0 | 1 | 1.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.315 | 0.45833 | 0.52083 | 0.58333 | 0.70833 | 0.83333 | 1.0208 | 1.0833 | 0.45833 | 1.0833 | 0.45833
| 1.5 | 1.9 | 6.5 | 5.5 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9 | 0.54167 | 0.625 | 0 | 0.47917 | 0 | 0 | 0 | 1.25 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.66 | 0.45833 | 0.57333 | 0.64583 | 0.77083 | 0.89583 | 1.0833 | 1.1825 | 0.45833 | 1.1825 | 0.45833
| 2 | 2.375 | 10.5 | 10.5 | 0 | 11.5 | 0 | 14.5 | 17.75 | 2 | 2.375 | 0.58333 | 0.70833 | 0 | 0.95833 | 0 | 1.2083 | 1.49 | 1.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.9 | 0.54167 | 0.625 | 0.70833 | 0.83333 | 0.95833 | 1.1458 | 1.2817 | 0.54167 | 1.2817 | 0.54167
| 2.5 | 2.875 | 7.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.875 | 0.625 | 0.79167 | 0 | 0.79167 | 0 | 0 | 0 | 2 | 2.375 | 0.91667 | 0.91667 | 0 | 0.91667 | 0.91667 | 0.91667 | 1.25 | 2 | 2.375 | 0.58333 | 0.70833 | 0.95833 | 0.95833 | 1.2083 | 1.2083 | 1.4792 | 2 | 2.375 | 0.58333 | 0.70833 | 0.79167 | 0.95833 | 1.125 | 1.2083 | 1.4792 | 0.58333 | 1.4792 | 0.58333
| 3 | 3.5 | 13 | 13 | 0 | 14 | 18.5 | 18.5 | 0 | 3 | 3.5 | 0.66667 | 0.9275 | 0 | 1.1667 | 1.25 | 1.5417 | 1.9167 | 2.5 | 2.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.875 | 0.625 | 0.79167 | 1 | 1.0625 | 1.2292 | 1.375 | 1.7608 | 0.625 | 1.7608 | 0.625
| 4 | 4.5 | 14 | 14 | 16 | 17 | 21.5 | 21.5 | 26.5 | 4 | 4.5 | 0.75 | 1 | 1.3333 | 1.4167 | 1.5 | 1.7917 | 2.24 | 3 | 3.5 | 1.0417 | 1.0417 | 0 | 1.0417 | 1.125 | 1.125 | 1.5 | 3 | 3.5 | 0.66667 | 0.92708 | 1.1667 | 1.1667 | 1.25 | 1.5417 | 1.8958 | 3 | 3.5 | 0.66667 | 0.92708 | 1.125 | 1.1667 | 1.25 | 1.5417 | 1.8958 | 0.66667 | 1.8958 | 0.66667
| 6 | 6.625 | 18 | 18 | 19.5 | 18 | 18 | 27.6 | 36 | 6 | 6.625 | 0.875 | 1.3233 | 1.625 | 1.8333 | 2 | 2.3125 | 3.0417 | 3.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 4 | 0.70833 | 0.96417 | 1.25 | 1.2917 | 1.375 | 1.6667 | 2.0525 | 0.70833 | 2.0525 | 0.70833
| 8 | 8.625 | 20.5 | 20.25 | 23.5 | 20.5 | 20.5 | 32.75 | 40.25 | 8 | 8.625 | 0.95833 | 1.375 | 1.9583 | 2.1667 | 2.4167 | 2.7292 | 3.4067 | 4 | 4.5 | 1.1667 | 1.1667 | 1.1667 | 1.1667 | 1.25 | 1.25 | 1.6667 | 4 | 4.5 | 0.75 | 1 | 1.3333 | 1.4167 | 1.5 | 1.7917 | 2.2083 | 4 | 4.5 | 0.75 | 1 | 1.3333 | 1.4167 | 1.5 | 1.7917 | 2.2083 | 0.75 | 2.2083 | 0.75
| 10 | 10.75 | 18 | 22 | 26.5 | 24 | 24 | 39 | 50 | 10 | 10.75 | 1.0833 | 1.5 | 2.2083 | 2.5833 | 2.75 | 3.25 | 4.24 | 5 | 5.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.563 | 1 | 1.1617 | 1.4792 | 1.625 | 1.75 | 2.0525 | 2.6042 | 1 | 2.6042 | 1
| 12 | 12.75 | 19.75 | 25 | 30 | 28 | 38 | 44.5 | 56 | 12 | 12.75 | 1.1667 | 1.6458 | 2.5 | 2.75 | 3.1667 | 3.7083 | 4.74 | 6 | 6.625 | 1.5 | 1.5 | 1.5 | 1.5 | 1.6667 | 1.6667 | 2 | 6 | 6.625 | 1.2917 | 1.3229 | 1.625 | 1.8333 | 2 | 2.3125 | 3 | 6 | 6.625 | 1.2917 | 1.3229 | 1.625 | 1.8333 | 2 | 2.3125 | 3 | 1.2917 | 3 | 1.2917
| 14 | 14 | 27 | 30 | 0 | 30 | 0 | 0 | 0 | 14 | 14 | 2.25 | 2.5 | 0 | 2.9167 | 0 | 0 | 0 | 8 | 8.625 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.9583 | 1.9583 | 2.3333 | 8 | 8.625 | 1.5 | 1.6458 | 1.9583 | 2.1667 | 2.4167 | 2.7292 | 3.375 | 8 | 8.625 | 1.5 | 1.6458 | 1.9583 | 2.1667 | 2.4167 | 2.7292 | 3.375 | 1.5 | 3.375 | 1.5
| 16 | 16 | 30 | 33 | 0 | 33 | 44.5 | 54.5 | 65 | 16 | 16 | 2.5 | 2.75 | 0 | 3.25 | 3.7083 | 4.5417 | 5.4167 | 10 | 10.75 | 1.9583 | 1.9583 | 1.9583 | 1.9583 | 2.125 | 2.125 | 2.75 | 10 | 10.75 | 1.75 | 1.8646 | 2.2083 | 2.5833 | 2.75 | 3.25 | 4.1667 | 10 | 10.75 | 1.75 | 1.8646 | 2.2083 | 2.5833 | 2.75 | 3.25 | 4.1667 | 1.75 | 4.1667 | 1.75
| 18 | 18 | 34 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 18 | 2.8333 | 0 | 0 | 3.5833 | 0 | 0 | 0 | 12 | 12.75 | 2.2083 | 2.2083 | 2.2083 | 2.2083 | 2.4583 | 2.4583 | 3 | 12 | 12.75 | 2 | 2.125 | 2.5 | 2.75 | 3.1667 | 3.7083 | 4.6667 | 12 | 12.75 | 2 | 2.125 | 2.5 | 2.75 | 3.1667 | 3.7083 | 4.6667 | 2 | 4.6667 | 2
| 20 | 20 | 36 | 39 | 0 | 47 | 52 | 0 | 0 | 20 | 20 | 3 | 3.25 | 0 | 3.9167 | 4.3333 | 0 | 0 | 14 | 14 | 2.375 | 2.375 | 2.375 | 2.375 | 2.625 | 2.625 | 0 | 14 | 14 | 2.25 | 2.5 | 2.7083 | 2.9167 | 3.375 | 4.125 | 0 | 14 | 14 | 2.25 | 2.5 | 2.7083 | 2.9167 | 3.375 | 4.125 | 5.0833 | 2.25 | 5.0833 | 2.25
| 24 | 24 | 42 | 45 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 3.5 | 3.75 | 0 | 4.5833 | 0 | 0 | 0 | 16 | 16 | 2.5417 | 2.5417 | 2.5417 | 2.5417 | 2.7917 | 2.7917 | 0 | 16 | 16 | 2.5 | 2.75 | 2.9583 | 3.25 | 3.7083 | 4.5417 | 0 | 16 | 16 | 2.5 | 2.75 | 2.9583 | 3.25 | 3.7083 | 4.5417 | 5.5 | 2.5 | 5.5 | 2.5
| 30 | 30 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 2.7917 | 2.7917 | 2.7917 | 2.7917 | 3.0417 | 3.0417 | 0 | 18 | 18 | 2.8333 | 3 | 3.2083 | 3.5833 | 4 | 5.0417 | 0 | 18 | 18 | 2.8333 | 3 | 3.2083 | 3.5833 | 4 | 5.0417 | 5.9167 | 2.8333 | 5.9167 | 2.8333
[19 empty] | 20 | 20 | 2.9583 | 2.9583 | 2.9583 | 2.9583 | 3.2083 | 3.215 | 0 | 20 | 20 | 3 | 3.25 | 3.4583 | 3.9167 | 4.3333 | 5.4583 | 0 | 20 | 20 | 3 | 3.25 | 3.4583 | 3.9167 | 4.3333 | 5.4583 | 6.3333 | 3 | 6.3333 | 3
[19 empty] | 22 | 22 | 3.2083 | 3.2083 | 3.2083 | 3.2083 | 0 | 0 | 0 | 22 | 22 | 3.3333 | 3.5833 | 3.75 | 4.25 | 0 | 0 | 0 | 22 | 22 | 3.3333 | 3.5833 | 3.75 | 4.25 | 4.7083 | 5.9167 | 6.75 | 3.3333 | 6.75 | 3.3333
[19 empty] | 24 | 24 | 3.5 | 3.5 | 3.5 | 3.5 | 3.75 | 3.75 | 0 | 24 | 24 | 3.5 | 2 | 4.0417 | 4.5833 | 5.0833 | 6.375 | 0 | 24 | 24 | 3.5 | 3.75 | 4.0417 | 4.5833 | 5.0833 | 6.375 | 7.1667 | 3.5 | 7.1667 | 3.5
[19 empty] | 26 | 26 | 3.7083 | 3.7083 | 3.7083 | 3.7083 | 0 | 0 | 0 | 26 | 26 | 3.75 | 4.0833 | 4.5417 | 4.75 | 0 | 0 | 0 | 26 | 26 | 3.75 | 4.0833 | 4.5417 | 4.75 | 5.6667 | 6.875 | 7.5833 | 3.75 | 7.5833 | 3.75
[19 empty] | 30 | 30 | 4.0833 | 4.0833 | 4.0833 | 4.0833 | 4.3333 | 0 | 0 | 30 | 30 | 4.25 | 4.5833 | 5 | 5.4167 | 6.25 | 0 | 0 | 30 | 30 | 4.25 | 4.5833 | 5 | 5.4167 | 6.25 | 7.375 | 8 | 4.25 | 8 | 4.25
[19 empty] | 34 | 34 | 4.5417 | 4.5417 | 4.5417 | 4.5417 | 0 | 0 | 0 | 34 | 34 | 4.8333 | 5.3333 | 5.8333 | 6.3333 | 0 | 0 | 0 | 34 | 34 | 4.8333 | 5.3333 | 5.8333 | 6.3333 | 6.875 | 7.875 | 8.4167 | 4.8333 | 8.4167 | 4.8333
[19 empty] | 36 | 36 | 4.7083 | 4.7083 | 4.7083 | 4.7083 | 4.9583 | 0 | 0 | 36 | 36 | 5 | 5.6667 | 6.1667 | 6.8333 | 7.5 | 0 | 0 | 36 | 36 | 5 | 5.6667 | 6.1667 | 6.8333 | 7.5 | 8.3333 | 8.8333 | 5 | 8.8333 | 5
[19 empty] | 42 | 42 | 5.5417 | 5.5417 | 5.5417 | 5.5417 | 0 | 0 | 0 | 42 | 42 | 6 | 6.3333 | 6.75 | 6.9167 | 0 | 0 | 0 | 42 | 42 | 6 | 6.3333 | 6.75 | 6.9167 | 8.3333 | 8.8333 | 9.25 | 6 | 9.25 | 6
| Feature | Length Lookup
| Valve | Rating Class 150 LB (285 psi)
Rating Class 300 LB (740 psi)
Rating Class 400 LB (990 psi)
Rating Class 600 LB (1480 psi)
Rating Class 900 LB (2220 psi)
Rating Class 1500 LB (3705 psi)
Rating Class 2500 LB (6170 psi)
Less than Rating Class 150 LB (285 psi)
Greater than Rating Class 2500 LB (6170 psi)
Unknown Rating Class

## Records Matrix - NWE (hidden)
Outside Diameter |  | Before Construction (BC) | [8 empty] | After Construction (AC)
|  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (Pipe) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
Before Contstruction | Pipe Specification | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Bill of Materials | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Purchase Order | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Pressure Test Plan | [11 empty] | x | x | x | x | x | x | x | x | x
Weld Procedures
| Material Transfer/Delivery Tags | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
Design/Contract Specifications
Job Estimate Face Sheet
| Invoices | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
After Construction | (MTR) Mill Test Report | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x
Material Inspection Report
| Pressure Test Report | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x | x | x | x | x | x
| As-Built Redlines | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
| As-Built Survey Notes | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
| As-Built Drawings | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
| Completion Report | x | x | x | x |  | x |  |  | x |  |  | x | x | x | x |  | x | x | x | x
| Pipeline Inspection Report | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x |  | x | x | x
| Pipeline Replacement Report | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x | x
| ILI Report | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x |  | x
| NDE Reports (X-Ray/UT) | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x | x | x
Weld Map/Detail
ASME History of Line Pipe (North America)
Pipe Manufacturer
Pipe Manufactured year
Specified Minimum Yield Strength (GRADE) |  | Before Construction (BC) | [8 empty] | After Construction (AC)
|  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (Pipe) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
Before Contstruction | Pipe Specification | [9 empty] | x |  | x | x | x | x | x |  | x
| Bill of Materials | [9 empty] | x |  | x | x | x | x | x |  | x
| Purchase Order | [9 empty] | x |  | x | x | x | x | x |  | x
| Pressure Test Plan | [12 empty] | x | x | x | x |  | x
Weld Procedures
| Material Transfer/Delivery Tags | [9 empty] | x |  | x | x | x | x | x |  | x
Design/Contract Specifications
Job Estimate Face Sheet
| Invoices | [9 empty] | x |  | x | x | x | x | x | x | x
After Construction | (MTR) Mill Test Report | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x |  |  | x |  |  | x
Material Inspection Report
| Pressure Test Report | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x
| As-Built Redlines | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x
| As-Built Survey Notes | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x
| As-Built Drawings | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x
| Completion Report | x | x | x | x |  | x |  |  | x |  |  |  | x | x | x |  |  | x
| Pipeline Inspection Report | [8 empty] | x |  |  |  | x | x | x
| Pipeline Replacement Report | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x
ILI Report
NDE Reports (X-Ray/UT)
| Weld Map/Detail | [9 empty] | x
ASME History of Line Pipe (North America)
Pipe Manufacturer
Pipe Manufactured year
Wall Thickness |  | Before Construction (BC) | [8 empty] | After Construction (AC)
|  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (Pipe) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
Before Contstruction | Pipe Specification | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Bill of Materials | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Purchase Order | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
| Pressure Test Plan | [12 empty] | x | x | x | x | x | x
Weld Procedures
| Material Transfer/Delivery Tags | [9 empty] | x |  | x | x | x | x | x |  | x | x | x
Design/Contract Specifications
Job Estimate Face Sheet
| Invoices | [9 empty] | x |  | x | x | x | x | x | x | x | x | x
After Construction | (MTR) Mill Test Report | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x | x | x | x | x | x
Material Inspection Report
| Pressure Test Report | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x |  |  | x | x | x
| As-Built Redlines | x | x | x | x |  | x |  |  | x | x |  | x |  | x |  | x | x | x | x | x
| As-Built Survey Notes | x | x | x | x |  | x |  |  | x | x |  | x | x |  |  | x | x | x | x | x
| As-Built Drawings | x | x | x | x |  | x |  |  | x | x |  | x |  |  |  | x | x | x | x | x
| Completion Report | x | x | x | x |  | x |  |  | x | x |  |  | x | x | x |  | x | x | x | x
| Pipeline Inspection Report | x | x | x | x |  |  |  |  | x | x |  |  | x | x | x | x |  | x | x
| Pipeline Replacement Report | x | x | x | x |  | x |  |  | x | x |  | x | x | x | x | x | x |  | x
| ILI Report | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x | x | x
| NDE Reports (X-Ray/UT) | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x
Weld Map/Detail
ASME History of Line Pipe (North America)
Pipe Manufacturer
Pipe Manufactured year
Seam Weld Type |  | Before Construction (BC) | [8 empty] | After Construction (AC)
|  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (Pipe) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report | ILI Report | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
Before Contstruction | Pipe Specification | [9 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
| Bill of Materials | [9 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
| Purchase Order | [9 empty] | x |  |  | x | x | x | x |  | x |  |  |  | x
| Pressure Test Plan | [9 empty] | x |  |  | x | x | x | x |  | x
Weld Procedures
| Material Transfer/Delivery Tags | [21 empty] | x
Design/Contract Specifications
Job Estimate Face Sheet
| Invoices | [9 empty] | x |  |  | x | x | x | x | [5 empty] | x
After Construction | (MTR) Mill Test Report | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  |  | x
Material Inspection Report
| Pressure Test Report | [12 empty] | x | x | x |  |  | x
| As-Built Redlines | x | x | x | x |  |  |  |  | x | x |  | x |  | x |  | x |  | x |  |  |  | x
| As-Built Survey Notes | x | x | x | x |  |  |  |  | x | x |  | x | x |  |  | x |  | x |  |  |  | x
| As-Built Drawings | x | x | x | x |  |  |  |  | x | x |  | x |  |  |  | x |  | x |  |  |  | x
| Completion Report | x | x | x | x |  |  |  |  | x |  |  |  | x | x | x |  |  | x |  |  |  | x
Pipeline Inspection Report
| Pipeline Replacement Report | x | x | x | x | [5 empty] | x |  | x | x | x | x | x | [5 empty] | x
ILI Report
NDE Reports (X-Ray/UT)
Weld Map/Detail
| ASME History of Line Pipe (North America) | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x | x |  | x |  |  |  |  | x | x
| Pipe Manufacturer | [21 empty] | x
| Pipe Manufactured year | [21 empty] | x
Rating Class |  | Before Construction (BC) | [8 empty] | After Construction (AC)
|  | Pipe Specification | Bill of Materials | Purchase Order | Pressure Test Plan | Weld Procedures | Material Transfer/Delivery Tags | Design/Contract Specifications | Job Estimate Face Sheet | Invoices | (Pipe) Mill Test Report | Material Inspection Report | Pressure Test Report | As-Built Redlines | As-Built Survey Notes | As-Built Drawings | Completion Report | Pipeline Inspection Report | Pipeline Replacement Report |  | NDE Reports (X-Ray/UT) | Weld Map/Detail | ASME History of Line Pipe (North America) | Pipe Manufacturer | Pipe Manufactured Year
Before Contstruction | Pipe Specification | [9 empty] | x |  | x | x | x | x | x | x | x
| Bill of Materials | [9 empty] | x |  | x | x | x | x | x | x | x
| Purchase Order | [9 empty] | x |  | x | x | x | x | x | x | x
Pressure Test Plan
Weld Procedures
| Material Transfer/Delivery Tags | [9 empty] | x |  | x | x | x | x | x | x | x
Design/Contract Specifications
Job Estimate Face Sheet
| Invoices | [9 empty] | x |  | x | x | x | x | x | x | x
After Construction | (MTR) Mill Test Report | x | x | x |  |  | x |  |  | x |  |  | x | x | x | x | x | x | x
Material Inspection Report
| Pressure Test Report | x | x | x |  |  | x |  |  | x | x |  |  | x | x | x | x | x | x
| As-Built Redlines | x | x | x |  |  | x |  |  | x | x |  | x |  | x |  | x | x | x
| As-Built Survey Notes | x | x | x |  |  | x |  |  | x | x |  | x | x |  |  | x | x | x
| As-Built Drawings | x | x | x |  |  | x |  |  | x | x |  | x |  |  |  | x | x | x
| Completion Report | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x |  | x | x
| Pipeline Inspection Report | x | x | x |  |  | x |  |  | x | x |  | x | x | x | x | x |  | x
Pipeline Replacement Report
ILI Report
NDE Reports (X-Ray/UT)
Weld Map/Detail
ASME History of Line Pipe (North America)
Pipe Manufacturer
Pipe Manufactured year

## Records Summary
Table 1 Breakdown of Attributes Not Verified
From Station | To Station | Feature Type | Outside Diameter | Wall Thickness | Seam Weld | Grade | ANSI Rating | Pressure Test
0+00 | 0+02 | Fitting | No | No | No | No | No | Yes
0+02 | 0+54 | Pipe | No | No | No | No | No | Yes
0+54 | 0+56 | Fitting | No | No | No | No | No | Yes
0+56 | 1+73 | Pipe | No | No | No | No | No | Yes
1+75 | 1+87 | Pipe | No | No | No | No | No | Yes
1+87 | 6+12 | Pipe | No | No | No | No | No | Yes
6+12 | 6+13 | Pipe | No | No | No | No | No | Yes
6+13 | 10+94 | Pipe | No | No | No | No | No | Yes
10+94 | 11+28 | Pipe | Yes | Yes | No | Yes | No | Yes
11+28 | 13+18 | Pipe | No | No | No | No | No | Yes
13+18 | 13+23 | Pipe | Yes | Yes | No | Yes | No | Yes
13+23 | 13+75 | Pipe | No | No | No | No | No | Yes
13+75 | 13+77 | Pipe | No | No | No | No | No | Yes
13+77 | 15+44 | Pipe | No | No | No | No | No | Yes
15+44 | 16+66 | Pipe | No | No | No | No | No | Yes
16+66 | 34+24 | Pipe | No | No | No | No | No | Yes
34+24 | 34+36 | Pipe | Yes | Yes | No | Yes | No | Yes
34+36 | 35+95 | Pipe | No | No | No | No | No | Yes
35+95 | 38+04 | Pipe | No | No | No | No | No | Yes
38+04 | 58+66 | Pipe | No | No | No | No | No | Yes
58+66 | 58+68 | Pipe | No | No | No | No | No | Yes
58+68 | 67+19 | Pipe | No | No | No | No | No | Yes
67+19 | 67+21 | Pipe | No | No | No | No | No | Yes
67+21 | 68+12 | Pipe | No | No | No | No | No | Yes
68+14 | 71+14 | Pipe | No | No | No | No | No | Yes
71+14 | 75+03 | Pipe | No | No | No | No | No | Yes
75+03 | 76+71 | Pipe | No | No | No | No | No | Yes
76+71 | 76+73 | Pipe | No | No | No | No | No | Yes
76+73 | 76+76 | Pipe | No | No | No | No | No | Yes
76+76 | 76+81 | Pipe | Yes | Yes | No | Yes | No | Yes
76+81 | 96+19 | Pipe | No | No | No | No | No | Yes
96+19 | 96+21 | Pipe | No | No | No | No | No | Yes
96+21 | 96+30 | Pipe | No | No | No | No | No | Yes
96+30 | 96+53 | Pipe | Yes | Yes | No | Yes | No | Yes
96+53 | 104+41 | Pipe | No | No | No | No | No | Yes
104+41 | 104+43 | Pipe | No | No | No | No | No | Yes
104+43 | 105+38 | Pipe | No | No | No | No | No | Yes
105+38 | 105+40 | Pipe | No | No | No | No | No | Yes
105+40 | 111+65 | Pipe | No | No | No | No | No | Yes
111+65 | 111+89 | Pipe | No | No | No | No | No | Yes
111+89 | 122+80 | Pipe | No | No | No | No | No | Yes
122+80 | 122+82 | Pipe | No | No | No | No | No | Yes
122+82 | 122+85 | Pipe | No | No | No | No | No | Yes
122+85 | 122+91 | Pipe | Yes | Yes | No | Yes | No | Yes
122+91 | 133+83 | Pipe | No | No | No | No | No | Yes
133+83 | 135+37 | Pipe | No | No | No | No | No | Yes
135+37 | 135+39 | Pipe | No | No | No | No | No | Yes
135+39 | 143+00 | Pipe | No | No | No | No | No | Yes
143+00 | 148+82 | Pipe | No | No | No | No | No | Yes
148+82 | 148+84 | Pipe | No | No | No | No | No | Yes
148+84 | 148+84 | Pipe | No | No | No | No | No | Yes
148+84 | 150+84 | Pipe | No | No | No | No | No | Yes
150+84 | 151+07 | Pipe | No | No | No | No | No | Yes
151+09 | 151+87 | Pipe | No | No | No | No | No | Yes
151+87 | 151+89 | Pipe | No | No | No | No | No | Yes
151+89 | 151+91 | Pipe | No | No | No | No | No | Yes
151+91 | 151+96 | Pipe | Yes | Yes | No | Yes | No | Yes
151+96 | 160+59 | Pipe | No | No | No | No | No | Yes
160+59 | 162+29 | Pipe | No | No | No | No | No | Yes
162+29 | 174+68 | Pipe | No | No | No | No | No | Yes
174+68 | 174+76 | Pipe | Yes | Yes | No | Yes | No | Yes
174+76 | 177+16 | Pipe | No | No | No | No | No | Yes
177+16 | 177+22 | Pipe | Yes | Yes | No | Yes | No | Yes
177+22 | 192+08 | Pipe | No | No | No | No | No | Yes
192+08 | 192+15 | Pipe | Yes | Yes | No | Yes | No | Yes
192+15 | 192+19 | Pipe | No | No | No | No | No | Yes
192+19 | 192+21 | Pipe | No | No | No | No | No | Yes
192+21 | 201+15 | Pipe | No | No | No | No | No | Yes
201+15 | 203+68 | Pipe | No | No | No | No | No | Yes
203+68 | 203+75 | Pipe | Yes | Yes | No | Yes | No | Yes
203+75 | 211+43 | Pipe | No | No | No | No | No | Yes
211+43 | 211+44 | Pipe | No | No | No | No | No | Yes
211+44 | 211+51 | Pipe | No | No | No | No | No | Yes
211+51 | 211+86 | Pipe | Yes | Yes | No | Yes | No | Yes
211+86 | 211+91 | Pipe | No | No | No | No | No | Yes
211+91 | 211+93 | Pipe | No | No | No | No | No | Yes
211+93 | 212+24 | Pipe | No | No | No | No | No | Yes
212+24 | 212+29 | Pipe | Yes | Yes | No | Yes | No | Yes
212+29 | 232+00 | Pipe | No | No | No | No | No | Yes
232+02 | 232+05 | Pipe | No | No | No | No | No | Yes
232+05 | 232+93 | Pipe | No | No | No | No | No | Yes
232+93 | 232+95 | Pipe | No | No | No | No | No | Yes
232+95 | 233+09 | Pipe | No | No | No | No | No | Yes
233+09 | 233+15 | Pipe | Yes | Yes | No | Yes | No | Yes
233+15 | 243+24 | Pipe | No | No | No | No | No | Yes
243+24 | 243+36 | Pipe | Yes | Yes | No | Yes | No | Yes
243+36 | 272+38 | Pipe | No | No | No | No | No | Yes
272+38 | 289+56 | Pipe | No | No | No | No | No | Yes
289+56 | 289+58 | Pipe | No | No | No | No | No | Yes
289+58 | 289+81 | Pipe | No | No | No | No | No | Yes
289+81 | 289+88 | Pipe | Yes | Yes | No | Yes | No | Yes
289+88 | 292+15 | Pipe | No | No | No | No | No | Yes
292+15 | 292+17 | Pipe | No | No | No | No | No | Yes
292+17 | 292+46 | Pipe | No | No | No | No | No | Yes
292+46 | 292+53 | Pipe | Yes | Yes | No | Yes | No | Yes
292+53 | 300+37 | Pipe | No | No | No | No | No | Yes
300+37 | 300+90 | Pipe | Yes | Yes | No | Yes | No | Yes
300+90 | 301+07 | Pipe | No | No | No | No | No | Yes
301+07 | 308+84 | Pipe | No | No | No | No | No | Yes
308+84 | 310+42 | Pipe | No | No | No | No | No | Yes
310+42 | 310+45 | Pipe | No | No | No | No | No | Yes
310+45 | 317+61 | Pipe | No | No | No | No | No | Yes
317+61 | 317+63 | Fitting | No | No | No | No | No | Yes